## Notification Sheet
Measurement Error Notification
Unique Reference Number (Allocated by Joint Office) |  | NW012
DN Reference | MER/UKD/190/15
Error Status | MER in Compilation
Brief Description | MTB Low DP transmitter failed its calibration check during procedure CP11.
Reason Measurement Error Detected | The measurement error was discovered during a routine validation.
Process Dates | Latest Notification Update | 2016-05-24 | dd/mm/yyyy
| Anticipated MER/SMER Publication |  | dd/mm/yyyy
Measurement Error Dates | Discovered | 2015-07-14 | dd/mm/yyyy
| First Notified |  | dd/mm/yyyy
| First Gas Day Where Error Present | 2015-04-21 | dd/mm/yyyy
| Last Gas Day Where Error Present | 2015-07-14 | dd/mm/yyyy
Offtake |  | Mickle Trafford MTA | MICKOF
Transporter | Upstream | National Grid – NTS
| Downstream | National Grid – DN
Meter Type |  | Orifice
LDZ |  | NW
Average flow rates for the meter for the perceived duration of the Measurement Error (MCM/Day) |  | 1.16 | MCM/Day
Declared volume of error (MCM) |  | 0.165 | MCM
Estimated quantity of error (GWh) |  | 1.79 | GWh
Estimated Significance |  | Low | < 30 GWh
Over or Under Read? |  | Under
MCM = million cubic meters
Unless stated otherwise all volumes are for the real dry gas at ISO Standard Reference conditions of 15°C and 1.01325 bar.
Unless stated otherwise all energies are calculated using a gross calorific value for the real dry gas at ISO reference conditions of 15°C (combustion) and 15°C and 1.01325 bar (metering).

## Look Up Data
Look Up Table For Offtake Data
DN/NTS Offtake Meter(s) | Site Type | Short Code | Upstream Transporter/Supplier | Downstream Transporter | Downstream LDZ | Meter Type
(if applicable)
Aberdeen MTA | Offtake | ABEROF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Adnams | Network Entry | <none> | Adnams Bio Energy Limited | National Grid – DN (EA) | EA | Turbine
Alrewas EM MTD | Offtake | ALREOF | National Grid - NTS | National Grid - DN | EM | Orifice
Alrewas WM MTA | Offtake | ALRWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Alrewas WM MTA/MTB Combined | Offtake | ALRWOF | National Grid - NTS | National Grid - DN | WM | System
Alrewas WM MTB | Offtake | ALRWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Armadale MTA | Offtake | ARMAOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Aspley MTA | Offtake | ASPYOF | National Grid - NTS | National Grid - DN | WM | Orifice
Asselby 38B MRC | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Asselby 38B MRD | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRA | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRB | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Atherstone MRA | Inter LDZ Transfer | <none> | National Grid – DN (EM) | National Grid – DN (WM) | WM | Turbine
Atherstone MRA/MRB Combined | Inter LDZ Transfer | <none> | National Grid – DN (EM) | National Grid – DN (WM) | WM | System
Atherstone MRB | Inter LDZ Transfer | <none> | National Grid – DN (EM) | National Grid – DN (WM) | WM | Turbine
Audley NW (Crewe) MTC | Offtake | AUDNOF | National Grid - NTS | National Grid - DN | NW | Orifice
Audley WM (Dunkirk) MTD | Offtake | AUDWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Audley WM (Dunkirk) MTD/MTE Combined | Offtake | AUDWOF | National Grid - NTS | National Grid - DN | WM | System
Audley WM (Dunkirk) MTE | Offtake | AUDWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Austrey MTA | Offtake | AUSTOF | National Grid - NTS | National Grid - DN | WM | Orifice
Aylesbeare MUA | Offtake | AYLEOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Aylesbeare MUB | Offtake | AYLEOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Bacton MRD | Offtake | BADSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Baldersby MRA | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Baldersby MRB | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Balgray MTA | Offtake | BALGOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Bathgate UMA | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bathgate UMB | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bishop Aukland MTA | Offtake | BISHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Blaby MTA | Offtake | BLABOF | National Grid - NTS | National Grid - DN | EM | Orifice
Blackrod MTA | Offtake | BLACOF | National Grid - NTS | National Grid - DN | NW | Orifice
Blackrod MTA/MTB Combined | Offtake | BLACOF | National Grid - NTS | National Grid - DN | NW | System
Blackrod MTB | Offtake | BLACOF | National Grid - NTS | National Grid - DN | NW | Orifice
Blyborough MTA | Offtake | BLYBOF | National Grid - NTS | National Grid - DN | EM | Orifice
Bracknell MTA | Inter LDZ Transfer | <none> | Scotia Gas – DN (SE) | National Grid – DN (NT) | NT | Orifice
Braishfield A MTA | Offtake | BRAAOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Braishfield B MTB | Offtake | BRABOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Bredbury | Network Entry | <none> | Adnams Bio Energy Limited | National Grid – DN (NW) | NW | Rotary Displacement
Brisley MRA | Offtake | BRISOF | National Grid - NTS | National Grid - DN | EA | Turbine
Brisley MRA/MRB Combined | Offtake | BRISOF | National Grid - NTS | National Grid - DN | EA | System
Brisley MRB | Offtake | BRISOF | National Grid - NTS | National Grid - DN | EA | Turbine
Broxburn MTA | Offtake | BROXOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Burley Bank MTA | Offtake | BURLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Burnhervie | Offtake | BURNOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Caldecott MRB | Offtake | CALDOF | National Grid - NTS | National Grid - DN | EM | Turbine
Caldecott MTA | Offtake | CALDOF | National Grid - NTS | National Grid - DN | EM | Orifice
Caldecott MTA/MRB Combined | Offtake | CALDOF | National Grid - NTS | National Grid - DN | EM | System
Careston MRA | Offtake | CAREOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Chittering | Network Entry | <none> | Pretoria Energy Company Limited | National Grid – DN (EA) | EA | Rotary Displacement
Choakford MRA | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Choakford MRB | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Cirencester MRB | Offtake | CIRNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRB | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRA | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coldstream MTA | Offtake | COLDOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Corbridge MRA | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Corbridge MRB | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Cowpen Bewley MTA | Offtake | COWPOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Deanshanger | Inter LDZ Transfer | <none> | Scotia Gas – DN (SO) | National Grid – DN (EM) | EM | Turbine
Dowlais MUA | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Dowlais MUB | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Drointon UMA | Offtake | DRTNOF | National Grid - NTS | National Grid - DN | EM | Ultrasonic
Drointon UMA/UMB Combined | Offtake | DRTNOF | National Grid - NTS | National Grid - DN | EM | System
Drointon UMB | Offtake | DRTNOF | National Grid - NTS | National Grid - DN | EM | Ultrasonic
Drum MTA | Offtake | DRUMOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Dryborough Road | Inter LDZ Transfer | <none> | National Grid – DN (NT) | Scotia Gas – DN (SE) | SE | Insertion DP Device
Dunstall Green MRA | Inter LDZ Transfer | <none> | Scotia Gas – DN | National Grid – DN (NT) | NT | Turbine
Dyffryn Cladach MUA | Offtake | DYFNOF | National Grid – NTS | Wales & West Utilities - DN | WS | Ultrasonic
Dyffryn Cladach MUB | Offtake | DYFNOF | National Grid – NTS | Wales & West Utilities - DN | WS | Ultrasonic
Easton Grey MUA | Offtake | EGRYOF | National Grid – NTS | Wales & West Utilities - DN | SW | Ultrasonic
Easton Grey MUB | Offtake | EGRYOF | National Grid – NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ecclestone MTA | Offtake | ECCLOF | National Grid – NTS | National Grid – DN | NW | Orifice
Elton MTA | Offtake | ELTNOF | National Grid – NTS | Northern Gas Networks – DN | NO | Orifice
Evesham MTA | Offtake | EVESOF | National Grid – NTS | Wales & West Utilities - DN | SW | Turbine
Evesham MTB | Offtake | EVESOF | National Grid – NTS | Wales & West Utilities - DN | SW | Turbine
Farningham MTA | Offtake | FARNOF | National Grid – NTS | Scotia Gas – DN | SE | Orifice
Fiddington MUA | Offtake | FIDDOF | National Grid – NTS | Wales & West Utilities - DN | SW | Ultrasonic
Fiddington MUB | Offtake | FIDDOF | National Grid – NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ganstead MTA | Offtake | GANSOF | National Grid – NTS | Northern Gas Networks – DN | NE | Orifice
Gilwern MUA | Offtake | GILWOF | National Grid – NTS | Wales & West Utilities - DN | WS | Ultrasonic
Gilwern MUB | Offtake | GILWOF | National Grid – NTS | Wales & West Utilities - DN | WS | Ultrasonic
Glenmavis MTA | Offtake | GLENOF | National Grid – NTS | Scotia Gas – DN | SC | Orifice
Glenmavis MTC | Offtake | GLENOF | National Grid – NTS | Scotia Gas – DN | SC | Orifice
Gosberton MTA | Offtake | GOSBOF | National Grid – NTS | National Grid – DN | EM | Orifice
Great Wilbraham MTA | Offtake | GWILOF | National Grid – NTS | National Grid – DN | EA | Orifice
Guyzance MRA | Offtake | GUYZOF | National Grid – NTS | Northern Gas Networks – DN | NO | Orifice
Guyzance MRB | Offtake | GUYZOF | National Grid – NTS | Northern Gas Networks – DN | NO | Orifice
Hardwick | Offtake | HARDOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Hibaldstow | Network Entry | <none> | Merlin Nenewables Limited | National Grid – DN (EM) | EM | Rotary Displacement
Hinckley Town | Inter LDZ Transfer | <none> | National Grid – DN (EM) | National Grid – DN (WM) | WM | Insertion Turbine Device
Holkham | Network Entry | <none> | Egmere Energy Ljmited | National Grid – DN (EA) | EA | Rotary Displacement
Holmes Chapel MTA | Offtake | HOLMOF | National Grid – NTS | National Grid – DN | NW | Orifice
Horndon B MTA | Offtake | HORNOF | National Grid – NTS | National Grid – DN | NT | Orifice
Humbleton MRA | Offtake | HUMBOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Humbleton MRB | Offtake | HUMBOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Hume MRA | Offtake | HUMEOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Hume MRB | Offtake | HUMEOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Hydes Pastures MTB | Inter LDZ Transfer | <none> | National Grid – DN (EM) | National Grid – DN (WM) | WM | Orifice
Ilchester MUA | Offtake | ILCHOF | National Grid – NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ilchester MUB | Offtake | ILCHOF | National Grid – NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ipsden MTA | Offtake | IPDNOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Keld MRA | Offtake | KELDOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Kenn MTA | Offtake | KENNOF | National Grid – NTS | Wales & West Utilities - DN | SW | Turbine
Kenn MTB | Offtake | KENNOF | National Grid – NTS | Wales & West Utilities - DN | SW | Turbine
Kinknockie MRA | Offtake | KINKOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Kinknockie MRB | Offtake | KINKOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Kirkstead MRA | Offtake | KIRKOF | National Grid – NTS | National Grid – DN | EM | Turbine
Kirkstead MRA/MRB Combined | Offtake | KIRKOF | National Grid – NTS | National Grid – DN | EM | System
Kirkstead MRB | Offtake | KIRKOF | National Grid – NTS | National Grid – DN | EM | Turbine
Langholm MRA | Offtake | LANGOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Leamington MRA | Offtake | LEAMOF | National Grid – NTS | National Grid – DN | WM | Turbine
Leamington MRA/MRB Combined | Offtake | LEAMOF | National Grid – NTS | National Grid – DN | WM | System
Leamington MRB | Offtake | LEAMOF | National Grid – NTS | National Grid – DN | WM | Turbine
Lindholme | Network Entry | <none> | Vulcan Renewables Limited | National Grid – DN (EM) | EM | Rotary Displacement
Little Burdon MTA | Offtake | LBUROF | National Grid – NTS | Northern Gas Networks – DN | NO | Orifice
Littleton Drew MRA | Offtake | LTDWOF | National Grid – NTS | Wales & West Utilities - DN | SW | Turbine
Lockerbie MTA | Offtake | LOCKOF | National Grid – NTS | Scotia Gas – DN | SC | Orifice
Lower Quinton UMA | Offtake | LOWQOF | National Grid – NTS | National Grid – DN | WM | Ultrasonic
Lower Quinton UMA/UMB Combined | Offtake | LOWQOF | National Grid – NTS | National Grid – DN | WM | System
Lower Quinton UMB | Offtake | LOWQOF | National Grid – NTS | National Grid – DN | WM | Ultrasonic
Lupton MTA | Offtake | LUPTOF | National Grid – NTS | National Grid – DN | NW | Orifice
Luxborough Lane MTA | Offtake | LUXBOF | National Grid – NTS | National Grid – DN | NT | Orifice
Luxborough Lane MTA/MTB Combined | Offtake | LUXBOF | National Grid – NTS | National Grid – DN | NT | System
Luxborough Lane MTB | Offtake | LUXBOF | National Grid – NTS | National Grid – DN | NT | Orifice
Maelor MUA | Offtake | MAELOF | National Grid – NTS | Wales & West Utilities - DN | WN | Ultrasonic
Maelor MUB | Offtake | MAELOF | National Grid – NTS | Wales & West Utilities - DN | WN | Ultrasonic
Malpas MRA | Offtake | MALPOF | National Grid – NTS | National Grid – DN | NW | Turbine
Mappowder MTA | Offtake | MAPPOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Market Harborough MTA | Offtake | MKHBOF | National Grid – NTS | National Grid – DN | EM | Orifice
Martyr's Lane | Inter LDZ Transfer | <none> | Scotia Gas – DN (SE) | National Grid – DN (NT) | NT | Insertion DP Device
Matching Green MTA | Offtake | MTCHOF | National Grid – NTS | National Grid – DN | EA | Orifice
Melkinthorpe MRA | Offtake | MELKOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Mickle Trafford MTA | Offtake | MICKOF | National Grid – NTS | National Grid – DN | NW | Orifice
Milwich MTA | Offtake | MILWOF | National Grid – NTS | National Grid – DN | WM | Orifice
Minworth | Network Entry | <none> | Severn Trent Water Limited | National Grid – DN (WM) | WM | Rotary Displacement
Nether Howcleugh MRA | Offtake | NETHOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Nether Howcleugh MRB | Offtake | NETHOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Oak Avenue | Inter LDZ Transfer | <none> | National Grid – DN (NT) | Scotia Gas – DN (SE) | SE | Insertion DP Device
Pannal MTA | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Pannal MTB | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Partington MTA | Offtake | PART OF | National Grid - NTS | National Grid - DN | NW | Orifice
Paull MTA | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Paull MTB | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Peterborough Eye MTA | Offtake | PEYEOF | National Grid - NTS | National Grid - DN | EA | Orifice
Peterborough Eye MTA/MTB Combined | Offtake | PEYEOF | National Grid - NTS | National Grid - DN | EA | System
Peterborough Eye MTB | Offtake | PEYEOF | National Grid - NTS | National Grid - DN | EA | Orifice
Peters Green 1 MTA | Offtake | PGRNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green 1 MTA/MTB Combined | Offtake | PGRNOF | National Grid - NTS | National Grid - DN | NT | System
Peters Green 1 MTB | Offtake | PGRNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green 2 (South Mimms) MTC | Offtake | PGSMOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green 2 (South Mimms) MTC/MTD Combined | Offtake | PGSMOF | National Grid - NTS | National Grid - DN | NT | System
Peters Green 2 (South Mimms) MTD | Offtake | PGSMOF | National Grid - NTS | National Grid - DN | NT | Orifice
Pickering MTA | Offtake | PICKOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Pitcairngreen MRA | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pitcairngreen MRB | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Portsdown Hill | Entry Point | None |  | Scotia Gas - DN | SO | Turbine
Poundbury | Entry Point | None |  | Scotia Gas - DN | SO | Turbine
Pucklechurch MRA | Offtake | PUCKOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Pucklechurch MRB | Offtake | PUCKOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Rawcliffe MRA | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Rawcliffe MRB | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Roehampton Lane | Inter LDZ Transfer | <none> | Scotia Gas – DN (SE) | National Grid – DN (NT) | NT | Insertion DP Device
Ross WM MTA | Offtake | ROSSOF | National Grid - NTS | National Grid - DN | WM | Orifice
Ross-On-Wye MRA | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Ross-On-Wye MRB | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Roudham Heath MTA | Offtake | ROUDOF | National Grid - NTS | National Grid - DN | EA | Orifice
Royston MRA | Offtake | ROYSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Royston MRA/MRB Combined | Offtake | ROYSOF | National Grid - NTS | National Grid - DN | EA | System
Royston MRB | Offtake | ROYSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Rugby MTB | Offtake | RUGBOF | National Grid - NTS | National Grid - DN | WM | Orifice
Saltwick 1 | Offtake | SALTOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Samlesbury MTA | Offtake | SAMLOF | National Grid - NTS | National Grid - DN | NW | Orifice
Scampton | Network Entry | <none> | Grange Farm Energy Limited | National Grid – DN (EM) | EM | Rotary Displacement
Seabank MUA | Offtake | SEABOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Seabank MUB | Offtake | SEABOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Shorne MTA | Offtake | SHOROF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Shustoke MTA | Offtake | SHUSOF | National Grid - NTS | National Grid - DN | WM | Orifice
Silk Willoughby MRA | Offtake | SILKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Silk Willoughby MRA/MRB Combined | Offtake | SILKOF | National Grid - NTS | National Grid - DN | EM | System
Silk Willoughby MRB | Offtake | SILKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Sotterley | Network Entry | <none> | Biocore AD2 Limited | National Grid – DN (EA) | EA | Rotary Displacement
Soutra MTA | Offtake | SOUTOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
St Fergus MTA | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
St Fergus MTB | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRA | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRB | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stratford MRA | Offtake | STRAOF | National Grid - NTS | National Grid - DN | WM | Turbine
Stratford MRB | Offtake | STRAOF | National Grid - NTS | National Grid - DN | WM | Turbine
Sutton Bridge MRA | Offtake | SUTNOF | National Grid - NTS | National Grid - DN | EM | Turbine
Sutton Bridge MRA/MRB Combined | Offtake | SUTNOF | National Grid - NTS | National Grid - DN | EM | System
Sutton Bridge MRB | Offtake | SUTNOF | National Grid - NTS | National Grid - DN | EM | Turbine
Tatsfield MTA | Offtake | TATSOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Thornton Curtis MTA | Offtake | CURTOF | National Grid - NTS | National Grid - DN | EM | Orifice
Thrintoft MTA | Offtake | THRNOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Tow Law MRA | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Tow Law MRB | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Towton MTA | Offtake | TOWTOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Tur Langton MTA | Offtake | TURLOF | National Grid - NTS | National Grid - DN | EM | Orifice
Walesby MRA | Offtake | WSBYOF | National Grid - NTS | National Grid - DN | EM | Turbine
Walesby MRA/MRB Combined | Offtake | WSBYOF | National Grid - NTS | National Grid - DN | EM | System
Walesby MRB | Offtake | WSBYOF | National Grid - NTS | National Grid - DN | EM | Turbine
Warburton MTA | Offtake | WARBOF | National Grid - NTS | National Grid - DN | NW | Orifice
West Winch MTA | Offtake | WINCOF | National Grid - NTS | National Grid - DN | EA | Orifice
Weston Point MTB | Offtake | WESTOF | National Grid - NTS | National Grid - DN | NW | Orifice
Wetheral MTA | Offtake | WETHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Whitwell MTA | Offtake | WHITOF | National Grid - NTS | National Grid - DN | EA | Orifice
Whitwell MTA/MTB Combined | Offtake | WHITOF | National Grid - NTS | National Grid - DN | EA | System
Whitwell MTB | Offtake | WHITOF | National Grid - NTS | National Grid - DN | EA | Orifice
Widnes | Network Entry | <none> | Refood UK Limited | National Grid – DN (NW) | NW | Rotary Displacement
Winkfield 2 MTB | Offtake | WNKSOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Winkfield MTA | Offtake | WINKOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Winkfield NT MTC | Offtake | WINTOF | National Grid - NTS | National Grid - DN | NT | Orifice
Wytch Farm | Network Entry | <none> | Perenco | Scotia Gas - DN | SO | Orifice
Yelverton MTA | Offtake | YELVOF | National Grid - NTS | National Grid - DN | EA | Orifice
| Over/Under Indicator | Error Magnitude |  | Error Status
| Over | High | >= 50 GWh | Error Notified
| Under | Low | < 30 GWh | MER in Compilation
|  | Medium | >= 30, < 50 GWh | SMER in Compilation
MER Published
SMER Published
Awaiting First Available Invoice
Invoiced
Closed / No Rec Required

## Extract for Register
Unique Reference Number | DN Reference | Description | Offtake | LDZ | Downstream Transporter | Significance Low <30GWH Medium >=30<50GWh High >=50GWh | Declared volume of error (MCM) | Estimated quantity of error (GWh) | Discovered | Error First Notified | First Gas Day Where Error Present | Last Gas Day Where Error Present | Latest Notification Update | Latest Error Status | Live/ Closed
NW012 | MER/UKD/190/15 | MTB Low DP transmitter failed its calibration check during procedure CP11. | Mickle Trafford MTA | NW | National Grid – DN | Low | 0.165 | 1.79 | 2015-07-14 | 0 | 2015-04-21 | 2015-07-14 | 2016-05-24 | MER in Compilation | Live