## MER Register
Unique Reference Number | DN Reference | Description | Offtake | LDZ | Downstream Transporter | Significance Low <30GWH Medium >=30<50GWh High >=50GWh | Declared volume of error (MCM) | Estimated quantity of error (GWh) | Discovered | Error First Notified | First Gas Day Where Error Present or; | Last Known Good Gas Day | Last Gas Day Where Error Present | Latest Notification Update | Latest Error Status | Live/ Closed | Invoice issued by Xoserve
EA001 |  | Error in orifice plate measurement | Great Wilbraham MTA | EA | National Grid - DN | Low | 0.8 | 8.68 | 2009-08-18 | 2009-09-07 | 2007-10-12 |  | 2008-10-09 | 2011-01-19 | Invoiced | Closed
EA002 |  | Error in orifice plate measurement | Matching Green MTA | EA | National Grid - DN | Low |  | 0 | 2009-08-18 | 2009-09-07 | 2007-11-15 |  |  | 2010-10-13 | No Rec Required | Closed
EA003 |  | Error in orifice plate measurement | Peterborough Eye MTA | EA | National Grid - DN | Low |  | 2.73 | 2009-08-18 | 2009-09-07 | 2007-11-07 |  |  | 2011-01-19 | Invoiced | Closed
EA004 |  | Error in orifice plate measurement | Peterborough Eye MTB | EA | National Grid - DN | Low |  | 3.88 | 2009-08-18 | 2009-09-07 | 2007-11-07 |  |  | 2011-01-19 | Invoiced | Closed
EA005 |  | Error in orifice plate measurement | Roudham Heath MTA | EA | National Grid - DN | Low |  | 7.63 | 2009-09-07 | 2009-09-07 | 2009-08-18 |  |  | 2011-01-19 | Invoiced | Closed
EA006 |  | Error in orifice plate measurement | West Winch MTA | EA | National Grid - DN | Low |  | 3.84 | 2009-09-07 | 2009-09-07 | 2009-08-18 |  |  | 2011-01-19 | Invoiced | Closed
EA007 |  | Error in orifice plate measurement | Whitwell MTA | EA | National Grid - DN | Low |  | 22.37 | 2009-09-07 | 2009-09-07 | 2009-08-18 |  |  | 2011-01-19 | Invoiced | Closed
EA008 |  | Error in orifice plate measurement | Whitwell MTB | EA | National Grid - DN | Medium |  | 38.13 | 2009-09-07 | 2009-09-07 | 2009-08-18 |  |  | 2011-01-19 | Invoiced | Closed
EA009 |  | Error in orifice plate measurement | Yelverton MTB | EA | National Grid - DN | Low |  | 21.51 | 2010-04-06 | 2010-04-06 | 2009-08-18 |  |  | 2011-01-19 | Invoiced | Closed
EA010 | MER/UKD/178/11 | The tracker was upgraded to a chromatograph. The tracker was decommisioned in 27th July 2009 but the chromatograph that was installed to replace the tracker did not function correctly until 14th October 2010. | Royston MRA/MRB Combined | EA | National Grid - DN | Low | 0.445 | 4.8 | 2011-06-01 | 2009-07-27 | 2009-07-27 |  | 2010-10-14 | 2012-05-31 | No Rec Required | Closed | 2012-05-25
EA011 | MER/UKD/181/12 | CP13 failed during validation | Matching Green MTA | EA | National Grid - DN | Null | 0 | 0 | 2012-04-17 | 2012-08-20 | 2012-04-17 |  | 2012-04-17 | 2013-11-25 | No Rec Required | Closed
EA012 | MER/UKD/184/13 | Error in the temperature measurement caused by a poor connection on the probe. | Bacton MRD | EA | National Grid - DN | Low | 0.151 | 1.62 | 2013-08-04 | 2013-08-09 | 2013-05-27 |  | 2013-08-04 | 2014-03-26 | Invoiced | Closed | 2014-03-26
EA013 | MER/UKD/187/14 | Intermittent loss of turbine meter pulses | Bacton MRD | EA | National Grid - DN | Low | 0.059382 | 0.6334 | 2014-06-28 | 2014-10-09 | 2014-04-07 |  | 2014-10-10 | 2015-01-22 | Invoiced | Closed
EA014 | MER/UKD/189/15 | MTB Low DP transmitter s/n 94104115440200230 failed its calibration check during procedure CP11. | Whitwell MTB | EA | National Grid - DN | Low | 0.214 | 2.377 | 2015-06-15 | 2016-05-24 | 2014-07-08 |  | 2015-06-25 | 2018-02-26 | No Rec Required | Closed
EA015 | MER/CAD/199/19 | Incorrect K-factors were entered into the Omni flow computer, possibly due to an old configuration being entered or human error. | Royston MRA | EA | Cadent Gas Limited - DN | Low | 0.035245 | 0.39 | 2020-06-09 | 2020-09-18 | 2019-11-05 |  | 2020-06-09 | 2022-03-09 | Invoiced | Closed | 2022-01-27
EA016 | MER/CAD/201/20 | During the annual validation of the measurement system (in accordance with Joint Office of Gas Transporters procedure T/PR/ME/2 parts 1 to 3) on 24th January 2020, it was discovered that one of the meter k-factors had been incorrectly entered into the flow computer. | Westry | Extract for Register | Cadent | Low | TBC | TBC | 2020-01-24 | 2020-11-25 | 2018-05-01 | 2020-01-24 | 2019-12-23 | 2020-12-03 | No Rec Required | Closed
EA017 | MER/CAD/215/22 | Intermittent flow on USM | Westry | EA | Cadent Gas Limited - DN | Low | 0.01 | 0.5 | 2022-04-28 | 2022-04-28 | 2022-04-17 | N/A | 2022-04-28 | 2022-09-29 | MER Published | Live
EA018 | CAD\225\22 | The value for Atmospheric Pressure in the flow computer was changed incorrectly during the 2021 ME2. | Royston MRA/MRB Combined | EA | Cadent Gas Limited - DN | High | 15.074 | 164.65 | 2022-10-17 | 2022-10-20 | 2021-10-19 |  | 2022-10-17 | 2023-01-04 | Invoiced | Closed | 2023-01-26
EA019 | MER/CAD/226/22 | The incorrect orifice plate calibration reference temperature was entered into the Omni flow computer due to ambiguity between the environment temperature and the orifice plate surface temperature on the calibration certificate. The error is approximately -0.001217% which is approximately 100 times smaller than the 0.1% of daily flow required for a reconcilable MER. | Whitwell MTA | EA | Cadent Gas Limited - DN | Low | Null | Null | 2022-11-18 | 2022-12-29 | 2022-07-30 | N/A | 2022-12-01 | 2022-12-29 | No Rec Required | Closed
EA020 | MER/CAD/221/22 | Westry BNEF has a single 2” Sick FlowSic500 ultrasonic meter stream for measurement of gas exiting the grid entry unit (GEU) and entering the distribution network (referred to as Fiscal USM). A second 2” Sick FlowSic500 ultrasonic meter is located on the inlet to the GEU for process control (referred to in this report as Inlet USM). Propane injection is used to control the gas properties (e.g. calorific value, Wobbe number, etc.) to meet the requirements of the Gas Safety (Management) Regulations (GS(M)R). Gas that is not within specification is rejected by a diverter valve. During normal operation the Fiscal USM will read slightly higher (~49 Sm3/h) than the Inlet USM due to the addition of propane. | Westry | EA | Cadent | Low | 0.01651 | 0.18 | 2022-08-13 | 2022-05-29 | 2022-05-29 | 2022-05-28 | 2022-08-23 | 2023-01-18 | MER Published | Live
EA021 | MER/CAD/221/22 | Unaccredited previous calibration produced unsuitable correction factors on calibration certificate that were highlighted following most recent calibration | Chittering | EA | Cadent Gas Limited – DN (EA) | Low | 0.0184 | 0.199 | 2016-08-25 | 2016-11-17 | 2016-01-01 |  | 2021-03-30 | 2023-03-23 | MER Published | Live
EA022 | MER/CAD/233/23 | Erroneous readings on Fiscal meter | Barnes Farm | EA | Cadent | Low | 0.001462 | 0.016 | 2022-11-30 | 2022-11-30 | 2022-11-30 | TBC | 2023-02-13 | 2023-03-22 | MER Published | Live
EA023 | MER/CAD/237/23 | Erroneous readings on Fiscal meter | Biodynamic Nottingham | EA | Cadent | Low | 0.002247 | 0 | 2022-09-03 | 2022-09-03 | 2022-09-03 |  | 2022-09-04 | 2023-07-11 | MER Published | Live
EM001 |  | Error in orifice plate measurement | Alrewas EM MTD | EM | National Grid - DN | Medium |  | 47.14 | 2009-09-07 | 2009-09-07 | 2009-08-18 |  |  | 2011-01-19 | Invoiced | Closed
EM002 |  | Error in orifice plate measurement | Blaby MTA | EM | National Grid - DN | Low |  | 5.87 | 2009-09-07 | 2009-09-07 | 2009-08-18 |  |  | 2011-01-19 | Invoiced | Closed
EM003 |  | Error in orifice plate measurement | Caldecott MTA | EM | National Grid - DN | Low |  | 0 | 2009-09-07 | 2009-09-07 | 2009-08-18 |  |  | 2011-09-27 | No Rec Required | Closed
EM004 |  | Error in orifice plate measurement | Tur Langton MTA | EM | National Grid - DN | Low |  | 22.59 | 2009-09-07 | 2009-09-07 | 2009-08-18 |  |  | 2011-01-19 | Invoiced | Closed
EM005 |  | Error in orifice plate measurement | Blyborough MTA | EM | National Grid - DN | Low |  | 17.96 | 2010-04-06 | 2010-04-06 | 2009-08-18 |  |  | 2011-01-19 | Invoiced | Closed
EM006 | MER/UKD/188/14 | Failure of turbine meter | Deanshanger | EM | National Grid - DN | Low | 0.0252 | 0.2744 | 2014-12-03 | 2015-05-01 | 2014-12-03 |  | 2014-12-04 | 2015-06-24 | Invoiced | Closed | 2015-06-24
EM007 | MER/UKD/191/15 | Low range differential pressure transducer was faulty | Gosberton MTA | EM | Cadent Gas Limited | Low | 0.022682 | 0.25 | 2015-07-26 | 2016-05-25 | 2015-07-25 |  | 2015-07-29 | 2017-12-07 | Invoiced | Closed | 2017-09-26
EM008 | MER/UKD/193/16 | Inappropriate viscosity figure resident in the flow computer | Thornton Curtis MTA | EM | Cadent Gas Limited | Low | 2.45 | 27.21 | 2016-05-03 | 2016-06-27 | 2016-05-03 |  | 2016-05-06 | 2018-11-05 | Invoiced | Closed | 2018-10-24
EM009 | MER/CAD/204/21 | Orifice plate was installed in the incorrect orientation during the annual validation in May 2019. During the validation in May 2020 the plate was removed but the replacement plate was also installed in the incorrect orientation. An industry expert has been consulted and initial studies indicate that this will result in an SMER. | Alrewas EM MTD | EM | Cadent Gas Limited - DN | High | See Report | See Report | 2021-02-23 | 2021-02-26 | 2019-05-23 | N/A | 2021-02-23 | 2022-08-16 | Invoiced | Closed | 2022-09-27
EM010 | MER/CAD/211/21 | Drift of ultrasonic meter flow readings | Hemswell Cliff | EM | Cadent Gas Limited – DN (EM) | Low | 0.27543 | 3 | 2021-05-10 | 2021-09-13 | 2019-09-20 | N/A | 2021-05-11 | 2022-02-16 | Awaiting First Available Invoice | Closed
EM011 | MER/CAD/218/22 | Orifice Plate error caused by incorrect seating within carrier | Thornton Curtis MTA | EM | Cadent Gas Limited - DN | High | 75.93 | 839 | 2022-07-04 | 2022-07-07 | 2022-04-21 |  | 2022-07-04 | 2023-08-10 | Invoiced | Closed | 2023-07-26
EM012 | MER/CAD/216/22 | Intermittent flow on USM | Hemswell Cliff | EM | Cadent Gas Limited – DN (EM) | Low | 0.001 | 0.02 | 2022-04-01 | 2022-04-01 | 2022-03-31 | N/A | 2022-03-31 | 2022-09-29 | Invoiced | Closed | Biomethane
EM013 | MER/CAD/217/22 | Intermittent flow on USM | Stoke Bardolph 2 | EM | Cadent Gas Limited – DN (EM) | Low | 0.001 | 0.002 | 2022-03-31 | 2022-04-01 | 2022-03-30 |  | 2022-04-05 | 2022-09-29 | MER Published | Live
EM014 | MER/CAD/220/22 | Intermittent flow on USM - Propane contamination | Biodynamic Nottingham | EM | Cadent | Low | 0.001556 | 0.02 | 2022-07-03 | 2022-07-03 | 2022-07-03 | 2022-07-04 | 2022-07-04 | 2023-03-22 | MER Published | Live
EM015 | MER/CAD/223/22 | Intermittent flow on USM - Propane contamination | Stanton Bio | EM | Cadent | Low | 0.00045 | TBC | 0 | 0 | 2022-08-21 |  | 2023-02-19 | 2023-07-11 | MER Published | Live
NO001 |  | Bent orifice plate after impact from debri after high volume flows | Ganstead MTA | NO | Northern Gas Networks - DN | Low | 0.15932 | 1.7833 | 2008-12-30 | 2009-04-02 | 2008-12-03 |  | 2008-12-30 | 2012-02-24 | Invoiced | Closed | 2012-02-24
NO002 |  | Wrong K Factors entered in the Omni | Melkinthorpe MRA | NO | Northern Gas Networks - DN | Low |  | 2.5607 | 2009-07-07 | 2009-07-07 | 2009-05-11 |  |  | 2011-01-20 | Invoiced | Closed
NO003 |  | Turbine meter failure | Corbridge MRB | NO | Northern Gas Networks - DN | Low |  | 0.01164 | 2009-12-08 | 2009-12-23 | 2009-12-09 |  |  | 2011-11-18 | No Rec Required | Closed
NO004 |  | Turbine meter Failure | Tow Law MRA | NO | Northern Gas Networks - DN | Low |  | 0.10022 | 2010-02-24 | 2010-04-21 | 2010-02-24 |  |  | 2011-11-18 | No Rec Required | Closed
NO005 |  | Low DP Cell found out of tolerance | Elton MTA | NO | Northern Gas Networks - DN | Low | 0.7218 | 8.203 | 2010-01-20 | 2010-06-11 | 2008-05-15 |  | 2009-05-13 | 2012-10-24 | Invoiced | Closed | 2012-10-24
NO006 |  | Bishop Auckland AGI, Turbine meter flow computer operated with wrong set-up for approximately 57 minutes causing an under-registration of approximately 20% | Bishop Aukland MTA | NO | Northern Gas Networks - DN | Low |  | 2.893 | 2010-05-19 | 2010-05-19 | 2010-05-19 |  |  | 2011-11-18 | No Rec Required | Closed
NO007 |  | Failure of Turbine HF | Asselby 7B MRA | NO | Northern Gas Networks - DN | Low | 0.027509 | 0.1956 | 2010-06-16 | 2010-07-27 | 2010-06-16 |  | 2010-06-16 | 2011-08-24 | Invoiced | Closed | 2011-08-24
NO008 |  | Gas Passed through stream with spool piece unmetered | Baldersby MRB | NO | Northern Gas Networks - DN | Low |  | 0.08377 | 2010-11-28 | 2010-12-22 | 2010-11-28 |  |  | 2011-11-18 | No Rec Required | Closed
NO009 |  | Ruptured downstream pipework caused overrange of site metering and damage to turbine meter. | Asselby 7B MRB | NO | Northern Gas Networks - DN | Low | 0.28 | 3.142 | 2010-10-25 | 2011-02-18 | tbc |  | 2010-11-04 | 2014-04-11 | Invoiced | Closed | 2014-04-28
NO010 | MERNO010 | RTD ADC Drift | Coldstream MTA | NO | Northern Gas Networks - DN | Low | 0.29987 | 1.737 | 2013-10-22 | 2014-02-15 | 0 |  | 2014-10-30 | 2014-03-11 | Invoiced | Closed | 2014-08-27
NO011 | MERNO011 | Over range of meter system | Saltwick 1 | NO | Northern Gas Networks - DN | Low | 0.015625 | 0.17 | 2016-12-12 | 2017-05-11 | 2016-12-12 |  | 2016-12-12 | 2020-08-10 | No Rec Required | Closed
NO012 | MERNO012 | Temprature transmitter bias. | Bishop Aukland MTA | NO | Northern Gas Networks - DN | Low | Nul | Nul | 2018-10-19 | 2018-10-22 | Un-known | 2018-09-13 | 2018-10-22 | 2019-02-06 | No Rec Required | Closed
NO013 | MERNO013 | Low differential pressure transmitter | Coldstream MTA | NO | Northern Gas Networks - DN | Low | 0.06797 | 0.74 | 2018-11-20 | 2018-11-30 | Un-known |  | 2018-09-24 | 2020-08-10 | Invoiced | Closed | 2021-02-28
NO014 | MERNO014 | Possible ADC drift | Cowpen Bewley MTA | NO | Northern Gas Networks - DN | Low | 0.46805 | 5.3289 | 2020-08-18 | 2020-01-20 | 0 | 2020-03-03 | 2020-08-18 | 2021-01-28 | Invoiced | Closed | 2022-09-27
NO015 | MERNO015 | Errors in Gemini billed data. | Howdon Bio | NO | Northern Gas Networks - DN | Low | 0.044405 | 0.5 | 2016-04-01 | 2020-02-25 | 2016-04-01 | N/A | 2018-12-31 | 2021-03-22 | Invoiced | Closed | Biomethane
NO016 | MERNO016 | Intermittent missed pulses from rotary meter and errors in Gemini billed data. | Howdon Bio | NO | Northern Gas Networks - DN | Low | 0.31741 | 3.5 | 2019-04-16 | 2020-01-31 | 2019-03-27 | N/A | 2019-01-21 | 2021-03-22 | Invoiced | Closed | Biomethane
NO017 | Northern Gas Networks | Failed temprature transmitter | Bishop Aukland MTA | NO | Northern Gas Networks - DN | Low | 0.0017 | 0.189 | 2021-03-18 | 2021-03-19 | Unknown | 2020-10-22 | 2020-11-02 | 2021-07-23 | Invoiced | Closed | 2023-03-24
NT001 |  | Error in orifice plate measurement | Horndon B MTA | NT | National Grid - DN | Low |  | 0 | 2009-08-18 | 2009-09-07 | 2008-02-26 |  |  | 2011-01-19 | Invoiced | Closed
NT002 |  | Error in orifice plate measurement | Luxborough Lane MTA | NT | National Grid - DN | Low |  | 17.8 | 2009-08-18 | 2009-09-07 | 2007-06-19 |  |  | 2011-01-19 | Invoiced | Closed
NT003 |  | Error in orifice plate measurement | Luxborough Lane MTB | NT | National Grid - DN | Low |  | 0.67 | 2009-08-18 | 2009-09-07 | 2007-06-19 |  |  | 2011-01-19 | Invoiced | Closed
NT004 |  | Error in orifice plate measurement | Peters Green MTA | NT | National Grid - DN | Low |  | 14.29 | 2009-08-18 | 2009-09-07 | 2007-06-13 |  |  | 2011-01-19 | Invoiced | Closed
NT005 |  | Error in orifice plate measurement | Peters Green MTB | NT | National Grid - DN | Medium |  | 35.39 | 2009-08-18 | 2009-09-07 | 2007-06-21 |  |  | 2011-01-19 | Invoiced | Closed
NT006 |  | Error in orifice plate measurement | Peters Green 2 (South Mimms) MTC | NT | National Grid - DN | Medium |  | 42.98 | 2009-08-18 | 2009-09-07 | 2007-06-21 |  |  | 2011-01-19 | Invoiced | Closed | 2011-04-28
NT007 |  | Error in orifice plate measurement | Peters Green 2 (South Mimms) MTD | NT | National Grid - DN | Low |  | 5.94 | 2009-08-18 | 2009-09-07 | 2008-02-22 |  |  | 2011-01-19 | Invoiced | Closed | 2011-04-28
NT008 |  | The temperature sensor was reading about 5 degrees high. The error was caused by a bad connection between the sensor and the temperature transmitter. | Horndon B MTA | NT | National Grid - DN | High | 11.094 | 125 | 2010-07-07 | 2010-12-14 | 2008-07-31 |  | 2010-07-07 | 2011-09-27 | Invoiced | Closed | 2013-02-26
NT009 | MER/UKD/185/14 | Temperature transmitters failed during recalibration attempt. | Peters Green 2 (South Mimms) MTC/MTD Combined | NT | National Grid - DN | Low | 0.79946 | 8.68 | 2014-05-08 | 2014-05-22 | 2014-05-06 |  | 2014-06-09 | 2014-12-09 | Invoiced | Closed | 2014-12-29
NT010 | MER/CAD/196/19 | The MTA meter tube diameter (581.1605 mm or 22.880333”) was calculated from the average of 12 diameters (cross-sections W,X,Y,Z taken at points 1, 2 and 3. The X-1 value was incorrectly read as 22.863” instead of 22.868”. | Luxborough Lane MTA | NT | Cadent Gas Limited – DN | Low | -0.13 | -5.29 | 0 | 2020-09-18 | Approximately 2003 |  | 2020-06-10 | 2020-12-08 | No Rec Required | Closed |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NT011 | MER/CAD/205/21 | Incorrect K-factors were entered into the flow computer at meter installation. | Dunstall Green MRA | NT | Cadent Gas Limited – DN (NT) | Low | Null | Null | 2020-11-01 | 2021-08-26 | Circa 2004 |  | 2021-02-08 | 2021-08-26 | No Rec Required | Closed
NT012 | MER/CAD/208/21 | Incorrectly calculated fixed factors for carbon dioxide and isentropic exponent were entered into the flow computer. | Bracknell MTA | NT | Cadent Gas Limited – DN (NT) | Low | Null | Null | 2021-04-27 | 2022-01-05 | 2021-01-22 |  | 2021-06-01 | 2022-01-05 | No Rec Required | Closed
NW001 |  | Error in orifice plate measurement | Blackrod MTA | NW | National Grid - DN | High |  | 60.78 | 2009-08-18 | 2009-09-07 | 2007-07-16 |  |  | 2011-01-19 | Invoiced | Closed
NW002 |  | Error in orifice plate measurement | Blackrod MTB | NW | National Grid - DN | Low |  | 8.67 | 2009-08-18 | 2009-09-07 | 2007-07-20 |  |  | 2011-01-19 | Invoiced | Closed
NW003 |  | Error in orifice plate measurement | Ecclestone MTA | NW | National Grid - DN | Low |  | 4.63 | 2009-08-18 | 2009-09-07 | 2007-08-07 |  |  | 2011-01-19 | Invoiced | Closed
NW004 |  | Error in orifice plate measurement | Holmes Chapel MTA | NW | National Grid - DN | Low |  | 10.4 | 2009-08-18 | 2009-09-07 | 2007-07-10 |  |  | 2011-01-19 | Invoiced | Closed
NW005 |  | Error in orifice plate measurement | Mickle Trafford MTA | NW | National Grid - DN | Low |  | 7.25 | 2009-08-18 | 2009-09-07 | 2007-10-04 |  |  | 2011-01-19 | Invoiced | Closed
NW006 |  | Error in orifice plate measurement | Samlesbury MTA | NW | National Grid - DN | Low |  | 27.12 | 2009-08-18 | 2009-09-07 | 2007-08-22 |  |  | 2011-01-19 | Invoiced | Closed
NW007 |  | Error in orifice plate measurement | Warburton MTA | NW | National Grid - DN | Low |  | 29.84 | 2009-08-18 | 2009-09-07 | 2007-07-09 |  |  | 2011-01-19 | Invoiced | Closed
NW008 |  | Error in orifice plate measurement | Weston Point MTB | NW | National Grid - DN | Low |  | 2.87 | 2009-08-18 | 2009-09-07 | 2007-09-21 |  |  | 2011-01-19 | Invoiced | Closed
NW009 |  | The orifice plate bore diameter was incorrectly measured. The incorrect bore was entered into the flow computer configuration without taking the drain hole into account. | Blackrod MTA | NW | National Grid - DN | Low |  | 24.7 | 2009-09-01 | 2009-10-08 | 2004-08-17 |  |  | 2011-01-19 | Invoiced | Closed | 2013-01-25
NW010 |  | The effective orifice bore was corrected twice for the drain hole. | Weston Point MTB | NW | National Grid - DN | Low | 0.024293 | 0.2632 | 2011-10-05 | 2011-12-22 | 2011-08-25 |  | 2011-10-05 | 2013-01-17 | Invoiced | Closed | 2013-01-25
NW011 |  | Pressure transducer locking up | Blackrod MTB | NW | National Grid - DN | Low | 0.1217 | 1.34 | 2011-12-09 | 2011-12-23 | 2011-12-09 |  | 2011-12-09 | 2013-01-17 | Invoiced | Closed | 2017-09-26
NW012 | MER/UKD/190/15 | MTB Low DP transmitter failed its calibration check during procedure CP11. | Mickle Trafford MTA | NW | National Grid – DN | Low | 0.165 | 1.79 | 2015-07-14 | 2016-05-25 | 2015-04-20 |  | 2015-07-14 | 2017-12-04 | Invoiced | Closed
NW013 | MER/UKD/192/15 | Incorrect parameters were deployed in the flow computer configuration serving the Weston Point NTS to LDZ offtake following a metering separation project. | Weston Point MTB | NW | National Grid - DN | Low | null | null | 2015-09-14 | 2015-09-30 | 2015-08-25 |  | 2015-09-14 | 2018-02-26 | No Rec Required | Closed
NW014 | MER/CAD/198/18 | The ADC calibration shifted over the course of the year. | Holmes Chapel MTA | NW | Cadent Gas Limited – DN | Low | -0.135 | -0.0015 | 2019-06-24 | 2020-09-18 | 0 | 2018-06-29 | 2019-06-24 | 2021-07-06 | No Rec Required | Closed
NW015 | MER/CAD/200/19 | Orifice and tube calibration temperatures were interchanged at time of the ME2. | Mickle Trafford MTA | NW | Cadent Gas Limited – DN | Low | 0.00325 | 0.13 | 2020-08-12 | 2020-09-18 | 2020-07-08 | 2020-07-07 | 2020-08-12 | 2021-07-06 | No Rec Required | Closed
SC001 |  | Incorrect K-factors entered in OMNI flow computer | Langholm MRA | SC | Scotia Gas - DN | Low | 5.37 | 0.5 | 2008-11-21 | 2008-12-01 | 2005-11-07 |  | 2008-12-02 | 2010-03-09 | Invoiced | Closed | 2013-03-26
SC002 |  | GAUGE PRESSURE TRANSMITTER ERROR | Lockerbie MTA | SC | Scotia Gas - DN | Low | 0.09 | 0.5 | 2009-05-27 | 2010-01-21 | 2008-06-02 |  | 2009-05-27 | 2013-03-26 | Invoiced | Closed
SC003 |  | Calibration shift between calibrations | Langholm MRA | SC | Scotia Gas - DN | Low |  |  | 2010-01-19 | 2010-01-25 | 2008-12-02 |  | 2009-11-10 | 2012-10-24 | No Rec Required | Closed
SC004 |  | Failed ME2 Spin-Down Test. Report Will Be Forwarded To NG (UKT) As A 'Null Report' Hence No Entries In Flow Fields Below | Nether Howcleugh MRA | SC | Scotia Gas - DN | Low |  |  | 2009-09-29 | 2010-02-22 | 2009-03-09 |  |  | 2011-10-03 | No Rec Required | Closed
SC005 |  | Faulty turbine meter wiring | Careston MRA | SC | Scotia Gas - DN | Low | 0.0015 | 0.017 | 2010-08-22 | 2010-09-02 | 2010-08-22 |  | 2010-08-22 | 2014-12-09 | No Rec Required | Closed
SC006 |  | Incorrect orifice plate location in carrier | Aberdeen MTA | SC | Scotia Gas - DN | High | 292 | 3223 | 2010-08-10 | 2010-09-24 | 2009-07-21 |  | 2010-08-10 | 2013-12-03 | Invoiced | Closed | 2013-10-24
SC007 |  | LDP calibration error | Balgray MTA | SC | Scotia Gas - DN | Low | 0.265 | 2.9 | 2010-04-06 | 2010-12-23 | 2009-04-22 |  | 2010-04-06 | 2013-04-05 | Invoiced | Closed
SC008 |  | Incorrect OMNI k-factor at one frequency point | Bathgate UMA | SC | Scotia Gas - DN | Low | 0.025 | 0.3 | 2010-05-26 | 2011-01-06 | 2007-06-11 |  | 2010-05-26 | 2013-12-03 | No Rec Required | Closed
SC009 |  | Turbine meter failure (single meter tube site). NULL report expected as Gas Control provided estimated DVOL's. | Careston MRA | SC | Scotia Gas - DN | Low |  |  | 2010-12-24 | 2011-01-17 | 2010-12-24 |  | 2011-01-06 | 2014-07-02 | No Rec Required | Closed | 2014-05-28
SC010 |  | CALIBRATION SHIFT NOTED FOLLOWING CALIBRATION OF TURBINE METERS | St Fergus MTA | SC | Scotia Gas - DN | Low | 0.81488 | 4.5 | 2011-09-08 | 2011-11-08 | 2007-04-01 |  | 2011-04-29 | 2014-05-15 | Invoiced | Closed | 2014-05-28
SC011 |  | Turbine meter calibration shift | Pitcairngreen MRB | SC | Scotia Gas - DN | Low | 0.045217 | 0.5 | 2012-05-17 | 2012-08-10 | 2011-06-14 |  | 2011-06-28 | 2014-05-15 | Invoiced | Closed | 2013-12-27
SC012 |  | The turbine meters on both streams have been recalibrated. Errors at the lowest calibration point average -2.5% | Kinknockie MRA/MRB | SC | Scotia Gas - DN | Low | 2.1417 | 23.8 | 2012-09-04 | 2012-09-05 | 2007-04-01 |  | 2012-02-07 | 2013-12-18 | Invoiced | Closed
SC013 |  | Incorrect wiring connection of cords 2 & 3 transducers. | Benhervie | SC | Scotia Gas - DN | 0 | 0 | 0 | 2013-11-28 | 2013-11-28 | 2013-10-12 |  | 2013-11-29 | 2014-12-09 | No Rec Required | Closed | 2019-05-28
SC014 |  | Flow Temperature fault - surface mounted RT drifting out of calibration causing flow computer to perform incorrect density calculations resulting in incorrect flow readings. | Lockerbie MTA | SC | Scotia Gas – DN | Low | 1.9 | 21 | 2017-01-27 | 2017-02-07 | 2016-06-08 |  | 2017-01-27 | 2019-08-27 | Invoiced | Closed | 2019-03-26
SC015 |  | ADC drift was found on the Omni flow computer on all inputs due to continous site power failure problems. | Soutra MTA | SC | Scotia Gas - DN | Low | 0.114 | 1.24 | 2018-03-20 | 2018-06-15 | 2017-11-02 |  | 2018-03-20 | 2018-09-18 | Invoiced | Closed
SC016 | SGN | Glenmavis National Offtake, metering system was non-operational. For a period of approximately two/three days, estimated gas flow values were submitted until new site metering system was commissioned and validated. | Glenmavis MTA | SC | Scotia Gas – DN | Low | TBC | TBC | 2020-08-13 | 2020-08-13 | 2020-08-13 |  | TBC | n/a | No Rec Required | Closed
SE001 |  | Low dp cell output limited, preventing switchup to High cell | Tatsfield MTA | SE | Scotia Gas - DN | Low |  | -0.16 | 2009-06-15 | 2010-06-15 | 2009-04-30 |  |  | 2011-10-03 | No Rec Required | Closed
SE002 |  | Contamination on upstream face of orifice plate | Farningham MTA | SE | Scotia Gas - DN | Low |  |  | 2009-06-24 | 2009-08-21 | 2009-06-24 |  | 2009-06-24 | 2011-10-03 | No Rec Required | Closed
SE003 |  | HIGH DP TRANSMITTER ERROR | Shorne MTA | SE | Scotia Gas - DN | Low | 0.18 | 2 | 2008-07-14 | 2010-02-15 | 2008-07-15 |  | 2009-07-14 | 2012-10-24 | No Rec Required | Closed
SE004 |  | Metering maximum exceeded for short duration (<5minutes) - NULL report expected | Farningham MTA | SE | Scotia Gas - DN | Low |  |  | 2010-02-17 | 2011-01-10 | 2010-02-17 |  | 2010-02-17 | 2014-04-01 | No Rec Required | Closed | 2016-01-27
SE005 | FarnB001 | Incorrect K factor value applied in the Omni flow computer configuration at 150.4 Hz frequency range. The declared value is 719.352, however that applied in the OMNI is 619.352. | Farningham B | SE | Scotia Gas - DN | Low | Unknown | unknown | 2015-09-24 | 2015-10-09 | 2015-06-19 |  | 2015-09-24 | 2016-01-18 | Invoiced | Closed | 2019-11-26
SE006 |  | Flow metering pressure transmitter lost pressure, causing a flow measurement error over approx 4.5 hours. | Farningham MTA | SE | Scotia Gas – DN | Low | 0.71 | 7.9 | 2016-10-03 | 2016-10-06 | 2016-10-03 |  | 2016-10-03 | 2017-02-07 | Invoiced | CLosed
SE007 |  | Temperature transmitter output range incorrectly set | Isle of Grain | SE | Southern Gas Networks Plc | High | 7.91 | 85.63 | 2019-02-12 |  | 2018-06-19 | 2019-02-12 | 2019-02-12 | 2021-06-23 | MER Published | Closed | 2011-08-24
SO001 |  | Equalising valve on Orifice Plate impulse lines to Differential pressure transmitters open. | Braishfield B MTB | SO | Scotia Gas - DN | High |  | 1161 | 2010-01-26 | 2010-05-14 | 2010-04-26 |  |  | 2011-10-03 | Invoiced | Closed
SO002 |  | Low dp transmitter error | Braishfield A MTA | SO | Scotia Gas - DN | Low |  |  | 2010-01-21 | 2010-08-25 | 2009-12-31 |  | 2010-01-21 | 2014-03-24 | No Rec Required | Closed
SO003 |  | Low dp and pressure transmitter errors | Braishfield B MTB | SO | Scotia Gas - DN | Low |  |  | 2010-01-26 | 2010-08-25 | 2009-12-29 |  | 2010-01-26 | 2013-03-06 | No Rec Required | Closed | 2014-03-26
SO004 |  | Low DP transmitter error | Braishfield A MTA | SO | Scotia Gas - DN | Low | 0.433 | 4.7 | 2010-09-30 | 2011-01-10 | 2010-01-21 |  | 2010-09-30 | 2014-03-26 | Invoiced | Closed | 2014-04-28
SO005 |  | Errors on LDP, HDP, and Pressure transmitters | Braishfield B MTB | SO | Scotia Gas - DN | Low | 0.118 | 1.3 | 2010-06-15 | 2011-01-13 | 2010-01-26 |  | 2010-06-15 | 2014-04-11 | Invoiced | Closed | 2014-04-28
SO006 |  | Error on HDP transmitter | Braishfield B MTB | SO | Scotia Gas - DN | Low | 0.015 | 0.2 | 2010-04-27 | 2011-01-14 | 2010-04-25 |  | 2010-04-27 | 2014-04-11 | Invoiced | Closed | 2014-04-28
SO007 |  | HDP transmitter calibration error | Braishfield B MTB | SO | Scotia Gas - DN | Low | 1.082 | 11.7 | 2011-01-07 | 2011-01-20 | 2010-07-30 |  | 2011-01-07 | 2014-04-11 | Invoiced | Closed | 2014-11-26
SO008 |  | Stream 2 LDP ME2 results exceed tolerance. | Ipsden MTC | SO | Scotia Gas - DN | Low |  |  | 2011-05-20 | 2011-10-14 | 2010-05-21 |  | 2011-05-20 | 2014-11-20 | Invoiced | Closed
SO009 |  | Temperature Transmitter | Hardwick | SO | Scotia Gas - DN | Null | 0 | 0 | 2011-06-07 | 2011-10-19 | 2010-07-06 |  | 2011-06-07 | 2013-03-06 | No Rec Required | Closed | 2014-08-27
SO010 |  | LDP ZERO DRIFT EXCEEDED LOW FLOW CUT-OFF | Braishfield A MTA | SO | Scotia Gas - DN | Low | 0.384 | 4.2 | 2011-07-16 | 2011-10-21 | 2011-06-30 |  | 2011-07-16 | 2011-12-20 | Invoiced | Closed | 2014-03-26
SO011 |  | ME2 LDP Error | Braishfield A MTA | SO | Scotia Gas - DN | Low | 0.413 | 4.5 | 2011-06-30 | 2011-10-26 | 2010-10-01 |  | 2011-06-30 | 2014-03-25 | Invoiced | Closed
SO012 |  | FLOWRATE EXCEEDED SITE MAXIMUM. MINOR DAMAGE TO ORIFICE PLATE AND HDP CALIBRATION SHIFT. FLOW ABOVE SITE MAXIMUM CORRECTED BY GAS CONTROL AND NG WARWICK. REMAINING ERRORS WILL RESULT IN NULL REPORT | Hardwick | SO | Scotia Gas - DN | 0 |  | 0 | 2011-11-10 | 2011-11-10 | 2011-09-10 |  | 2011-09-15 | 2012-04-10 | No Rec Required | Closed
SO013 |  | ME2 calibration errors exceeding tolerance on low dp and pressure transmitters. The reported results are not supported by HPMIS or System Control data so no estimate is provided below. | Mappowder MTA | SO | Scotia Gas - DN | 0 | 0 | 0 | 2012-05-22 | 2012-07-06 | 2011-05-23 |  | 2012-05-22 | 2013-04-05 | No Rec Required | Closed
SW001 |  | Suspect Meter Fault. | Evesham MTA | SW | Wales & West Utilities - DN | Medium |  | 45.1 | 2008-11-05 | 2010-03-31 | 2007-12-20 |  |  | 2010-09-22 | Invoiced | Closed
SW002 |  | Pressure transducer locking up | Ilchester MTA | SW | Wales & West Utilities - DN | Low |  | 0.33 | 2009-03-03 | 2009-03-31 | 2009-03-03 |  |  | 2009-10-08 | No Rec Required | Closed
SW003 |  | Incorrect frequencies entered in Omni flow computer | Coffinswell MRA | SW | Wales & West Utilities - DN | Low |  | <0.01 | 2009-02-17 | 2009-07-08 | 2008-08-29 |  | 2009-04-30 | 2009-10-08 | No Rec Required | Closed
SW004 |  | Pressure transducer locking up | Seabank MTA | SW | Wales & West Utilities - DN | Low |  | 0.02 | 2009-04-15 | 2009-09-25 | 2009-04-15 |  |  | 2009-12-07 | No Rec Required | Closed
SW005 |  | Incorrect frequencies entered in Omni flow computer | Choakford MRA | SW | Wales & West Utilities - DN | Low | <0.001 | <0.01 | 2009-02-17 | 2009-10-27 | 2008-10-13 |  | 2009-04-30 | 2009-12-07 | No Rec Required | Closed
SW006 |  | Failed ADC checks | Evesham MTA | SW | Wales & West Utilities - DN | 0 | 0 | 0 | 2009-08-04 | 2010-03-02 | 2008-07-08 |  | 2009-08-04 | 2012-06-12 | No Rec Required | Closed | 2011-02-24
SW007 |  | Incorrect K factors used in flow computer | Littleton Drew MRA | SW | Wales & West Utilities - DN | Low |  | -0.17213 | 2010-03-01 | 2010-05-18 | 2009-07-14 |  |  | 2011-04-15 | Invoiced | Closed | 2011-04-28
SW008 |  | Degradation of Turbine meter caused under registration of flow | Ross-On-Wye MRA | SW | Wales & West Utilities - DN | Low |  | 2.8283 | 2009-06-25 | 2010-05-18 | 2008-08-11 |  |  | 2011-01-21 | Invoiced | Closed | 2011-04-28
SW009 |  | Failed validation checks for pressure transmitter and temperature ADC | Ross-On-Wye MRB | SW | Wales & West Utilities - DN | Low |  | 0.64052 | 2009-08-27 | 2010-05-18 | 2009-03-20 |  |  | 2011-04-21 | Invoiced | Closed | 2011-10-26
SW010 |  | Loss of range due to software error | Aylesbeare MTA | SW | Wales & West Utilities - DN | Low |  | 0.077 | 2010-05-12 | 2010-05-26 | 2010-05-12 |  |  | 2011-10-17 | Invoiced | Closed | 2011-08-24
SW011 |  | Incorrect density figures calculated due to mismeasured composition figures by the chromatograph. | Ross-On-Wye MRB | SW | Wales & West Utilities - DN | Low |  | 0.040578 | 2009-12-18 | 2010-09-13 | 2009-12-15 |  |  | 2010-10-06 | Invoiced | Closed | 2011-12-28
SW012 |  | Incorrect density figures calculated due to mismeasured composition figures by the chromatograph. | Ross-On-Wye MRB | SW | Wales & West Utilities - DN | Low | 0.00275 | 0.0286 | 2010-03-26 | 2010-09-13 | 2010-03-25 |  | 2010-03-25 | 2010-09-24 | Invoiced | Closed | 2011-10-26
SW013 |  | Pressure transducer locking up | Evesham MTB | SW | Wales & West Utilities - DN | Low |  | 25.1 | 2010-06-02 | 2010-09-22 | 2010-03-15 |  |  | 2011-10-17 | Invoiced | Closed | 2011-04-28
SW014 |  | Calibration shift between calibrations | Ross-On-Wye MRA | SW | Wales & West Utilities - DN | Low |  | 19.26 | 2010-09-16 | 2010-09-24 | 2009-03-20 |  |  | 2011-04-21 | Invoiced | Closed | 2011-08-24
SW015 |  | Pressure transducer locked up. | Ilchester MTA | SW | Wales & West Utilities - DN | Low |  | 0.261 | 2010-09-25 | 2010-10-04 | 2010-09-25 |  |  | 2011-09-26 | Invoiced | Closed | 2011-10-26
SW016 |  | Pressure Transducer locking up | Aylesbeare MTA | SW | Wales & West Utilities - DN | Low |  | 0.583 | 2010-10-25 | 2010-10-25 | 2010-10-24 |  |  | 2011-10-17 | Invoiced | Closed | 2011-06-24
SW017 |  | Low Differential Pressure transmitter failed (AF) annual validation check | Easton Grey MTA | SW | Wales & West Utilities - DN | Low |  | 0.36876 | 2010-08-04 | 2010-11-17 | 2009-06-25 |  |  | 2010-10-06 | Invoiced | Closed
SW018 |  | Faulty turbine meter wiring | Cirencester MRB | SW | Wales & West Utilities - DN | Low |  | 0.1 | 2010-11-17 | 2010-11-17 | 2010-11-14 |  |  | 2012-03-26 | No Rec Required | Closed | 2011-04-28
SW019 |  | Lock up of metering pressure headcell | Ross WM MTA | SW | Wales & West Utilities - DN | Low |  | 0.71021 | 2010-12-23 | 2010-12-23 | 2010-12-16 |  |  | 2011-04-21 | Invoiced | Closed | 2011-10-26
SW020 |  | Pressure transducer locked up. | Aylesbeare MTA | SW | Wales & West Utilities - DN | Low |  | 0.06 | 2011-04-18 | 2011-04-18 | 2011-04-11 |  |  | 2011-10-17 | Invoiced | Closed | 2012-12-28
SW021 |  | Pressure transducer locking up | Aylesbeare MTA | SW | Wales & West Utilities - DN | Low | 0.0331 | 0.36 | 2011-12-12 | 2011-12-21 | 2011-12-04 |  | 2011-12-04 | 2012-05-28 | Invoiced | Closed | 2013-03-26
SW022 | MER/WWU/SW022 | Fixed RD applied in flow computer for duration of tracker fault | Littleton Drew MRA | SW | Wales & West Utilities - DN | Low | 0.003959 | 0.04 | 2012-03-16 | 2012-02-17 | 2012-01-19 |  | 2012-04-11 | 2013-03-26 | Invoiced | Closed | 2013-07-23
SW023 | MER/WWU/SW023 | Pressure and temperature inputs left in override mode in Omni following maintenance | Pucklechurch MRA | SW | Wales & West Utilities - DN | Low | 0.14389 | 1.58 | 2012-08-13 | 2012-08-28 | 2012-06-01 |  | 2012-06-14 | 2013-07-16 | Invoiced | Closed | 2013-12-27
SW024 | MER/WWU/SW024 | Metering pressure transducer out of tolerance | Evesham MTB | SW | Wales & West Utilities - DN | Low | 0.37037 | 4.03 | 2012-09-04 | 2012-09-11 | 2011-07-28 |  | 2012-08-01 | 2013-12-18 | Invoiced | Closed
SW025 | MER/WWU/SW025 | Metering pressure transducer out of tolerance | Fiddington MTA | SW | Wales & West Utilities - DN | Low | 0 | 1.9 | 2012-09-04 | 2012-09-11 | 2011-08-22 |  | 2012-08-21 | 2012-10-11 | No Rec Required | Closed | 2014-05-28
SW026 | MER/WWU/SW026 | Metering low differential pressure transducer out of tolerance | Easton Grey MTA | SW | Wales & West Utilities - DN | Low | 0 | 7.1 | 2012-10-01 | 2012-11-19 | 2011-06-15 |  | 2012-06-21 | 2014-05-15 | Invoiced | Closed | 2013-04-25
SW027 | MER/WWU/SW027 | Faulty turbine meter wiring | Littleton Drew MRA | SW | Wales & West Utilities - DN | Low | 0 | 7.8 | 2012-12-03 | 2012-12-20 | 2012-11-21 |  | 2012-11-30 | 2013-04-16 | Invoiced | Closed | 2014-05-28
SW028 | MER/WWU/SW028 | Faulty turbine meter wiring | Littleton Drew MRA | SW | Wales & West Utilities - DN | Low | 0 | 7.22 | 2013-01-11 | 2013-01-30 | 2013-01-08 |  | 2013-01-08 | 2014-05-15 | Invoiced | Closed | 2014-02-26
SW029 | MER/WWU/SW029 and MER/WWU/SW030 | Omni Configuration and Wiring Error. The calculations also refer to SW030 which can be closed due to it being covered in MER/WWU/029/13 Rev O report produced by GL. | Kenn MTA and Kenn MTB | SW | Wales & West Utilities - DN | Low | 0.28666 | 3.119 | 2013-03-19 | 2013-05-14 | 2012-03-20 |  | 2013-03-16 | 2014-02-19 | Invoiced | Closed
SW030 | MER/WWU/SW030 | Omni Configuration and Wiring Error | Kenn MTB | SW | Wales & West Utilities - DN | 0 | 0 | 0 | 2013-03-19 | 2013-05-14 | 2013-03-16 |  | 2013-03-19 | 2013-05-14 | No Rec Required | Closed | 2014-08-27
SW031 | MER/WWU/SW031 | Failed validation checks on pressure transmitter, pressure ADC and temperature ADC | Evesham MTA & MTB | SW | Wales & West Utilities - DN | Low | 2.1523 | 12 | 2013-09-01 | 2014-04-30 | 2012-07-30 |  | 2013-07-23 | 2014-05-19 | Invoiced | Closed | 2016-03-24
SW032 | MER/WWU/SW032 | Failed validation checks on pressure ADC and temperature ADC | Aylesbeare MTA | SW | Wales & West Utilities - DN | Low | 0.93309 | 6 | 2014-08-08 | 2015-07-17 | 2013-03-14 |  | 2014-06-24 | 2015-10-23 | Invoiced | Closed | 2015-10-26
SW033 | MER/WWU/SW033 | Failed validation checks on pressure and temperature ADC's | Easton Grey MTA | SW | Wales & West Utilities - DN | Low | 0.3 | 6 | 2014-11-11 | 2015-07-17 | 2012-12-10 |  | 2014-10-01 | 2015-07-17 | Invoiced | Closed | 2016-04-26
SW034 | MER/WWU/SW034 | Failed validation checks on the temperature transmitter and the temperature ADC. | Kenn MTA | SW | Wales & West Utilities - DN | Low | 0.7 | 4 | 2015-10-13 | 2015-11-30 | 2014-03-06 |  | 2015-03-12 | 2016-01-25 | Invoiced | Closed
SW035 | MER/WWU/SW035 | Failed validation checks on the temperature and pressure ADC's. | Coffinswell MRA | SW | Wales & West Utilities - DN | Low | 0.048 | 0.34 | 2016-02-08 | 2016-09-22 | 2015-08-13 |  | 2016-02-08 | 2016-11-22 | No Rec Required | Closed
SW036 | WWU | Incorrect K Factors used in the Omni flow computer for the calculation of volume flow through the Offtake. K Factors incorrectly input after meters returned from calibration. Compilied meter error calculated at 0.073%, this MER is a Null report. | Fiddington MTA | SW | Wales & West Utilities - DN | Low | 0.002 | 3.87 | 2021-08-18 | 2021-08-18 | 2021-04-06 |  | 2021-08-18 | 2022-08-31 | No Rec Required | Closed
SW037 | WWU | Failed Validation checks on the Pressure ADC. Compiled meter error calculated at 0.0474%, this MER is a Null report. | Pucklechurch MTA | SW | Wales & West Utilities - DN | Low | 0.033 | 0.36 | 2021-10-04 | 2021-12-03 | 00/01/1900 | 2021-04-20 | 2021-10-04 | 2022-08-31 | No Rec Required | Closed
SW038 | MER/WWU/SW038 | Human error led to entering K-Factors and frequencies for both streams into the Omni flow computer incorrectly | Easton Grey MTA | SW | Wales & West Utilities - DN | Low | 0.52 | 5.49 | 2023-03-02 | 2023-04-21 | 2020-06-15 |  | 2023-04-18 | 2023-04-21 | MER Published | Live
SW039 | MER/WWU/SW039 | Data entry correction following meter flow signal failure. | Cirencester MRA | SW | Wales & West Utilities - DN | Low | 0.19946 | 2.17 | 2023-01-09 | 2023-04-28 | 2023-01-09 |  | 2023-03-09 | 2023-04-28 | MER Published | Live
WM001 |  | Error in orifice plate measurement | Alrewas WM MTA | WM | National Grid - DN | Low |  | 0 | 2009-08-18 | 2009-09-07 | 2008-05-15 |  |  | 2011-01-19 | Invoiced | Closed
WM002 | MER/WWU/WN002 | Ultrasonic meter from Maelor stream A failed calibration and required repair by manufacturer | Maelor MUA | WN | Wales & West Utilities - DN | Low | 0.91025 | 10 | 2016-10-27 | 2017-11-20 | 2014-04-01 | 2016-11-16 | 2019-05-13 | 2019-05-13 | Invoiced | Closed
WM003 |  | Error in orifice plate measurement | Audley (Dunkirk) MTE | WM | National Grid - DN | Low |  | 2.54 | 2009-08-18 | 2009-09-07 | 2007-09-27 |  |  | 2011-01-19 | Invoiced | Closed
WM004 |  | Error in orifice plate measurement | Austrey MTA | WM | National Grid - DN | Low |  | 9.77 | 2009-08-18 | 2009-09-07 | 2007-08-31 |  |  | 2011-01-19 | Invoiced | Closed
WM005 |  | Error in orifice plate measurement | Ross WM MTA | WM | National Grid - DN | Low |  | 5.08 | 2009-08-18 | 2009-09-07 | 2007-10-25 |  |  | 2011-01-19 | Invoiced | Closed
WM006 |  | Error in orifice plate measurement | Shustoke MTA | WM | National Grid - DN | Low |  | 4.35 | 2009-08-18 | 2009-09-07 | 2008-01-08 |  |  | 2011-01-19 | Invoiced | Closed | 2011-10-26
WM007 |  | Error in orifice plate measurement | Hydes Pastures MTA | WM | National Grid - DN | Low |  | 1.1 | 2009-10-07 | 2009-10-08 | 2007-02-07 |  |  | 2011-10-13 | Invoiced | Closed
WM008 |  | Pressure transmitter locking up | Ross WM MTA | WM | National Grid - DN | Low |  | 0.06 | 2009-10-19 | 2009-10-19 | 2009-10-17 |  |  | 2010-04-15 | Invoiced | Closed | 2011-06-24
WM009 |  | The chromatograph mismeasured the composition and an incorrect density was calculated. | Ross WM MTA | WM | National Grid - DN | Low |  | 0.000119 | 2009-12-17 | not known | 2009-12-15 |  |  | 2011-09-26 | Invoiced | Closed | 2011-07-26
WM010 |  | The chromatograph mismeasured the composition and an incorrect density was calculated. | Ross WM MTA | WM | National Grid - DN | Low |  | 0.55 | 2010-01-11 | 2010-01-11 | 2010-01-11 |  |  | 2011-08-09 | Invoiced | Closed | 2011-07-26
WM011 |  | Failure of interposing volume integrator relay to telemetry resulting in under billing (MER/UKD/173/10) | Lower Quinton UMA & UMB | WM | National Grid - DN | Low |  | 5.5 | 2011-01-21 | 2010-12-21 | 2010-12-21 |  |  | 2011-08-09 | Invoiced | Closed | 2011-12-28
WM012 |  | As a result of the failure of the autochangover system, the second cylinder of helium carrier gas was not brought on line. This depleted the first cylinder beyond that which could support the chromatograph. | Rugby MTA | WM | National Grid - DN | Low |  | 0.26056 | 2011-02-11 | 2011-03-02 | 2011-02-10 |  |  | 2012-02-28 | Invoiced | Closed
WM013 | MER/UKD/183/13 | Suspected temperature loop error | Hydes Pastures MTB | WM | National Grid - DN | 0.03% (NULL) | 0.007901 | 0 | 2012-01-10 | 2012-05-16 | 2011-02-18 |  | 2012-07-20 | 2014-02-25 | No Rec Required | Closed | 2013-10-24
WM014 | MER/UKD/182/13 | Incorrect flow computer firmware was used. | Atherstone MRA | WM | National Grid - DN | High | 12.11 | 131.9 | 2013-02-20 | 2013-02-21 | 2012-03-14 |  | 2013-02-20 | 2013-02-22 | Invoiced | Closed | 2019-05-03
WM015 | MER/CAD/194/15 | Two separate issues have contributed to the error – (1) At the time of validation, the flow pressure transmitter was found to have failed its T/PR/ME/2 parts 1 to 3 CP10 calibration check. The start date/time of this failure is unknown/ cannot be safety determined with sufficiently high probability, so the ‘last known good Gas Day’ principle as described in OAD Section D 5.2.3 applies for this part of the error. (2) The applied linearisation in the flow computer was found to be that for the atmospheric air calibration characteristic as opposed to that for high pressure natural gas. The period for this is well defined, so its full contribution applies for this particular aspect. | Minworth | WM | Cadent Gas Limited – DN (WM) | Low | 0.00902 | 0.10022 | 2015-09-01 | 2018-11-02 | 2014-09-24 | 2014-09-24 | 2015-09-01 | 2019-06-10 | Invoiced | Closed | 2019-05-03
WM016 | MER/CAD/195/18 | Intermittent erroneous readings from the custody transfer ultrasonic meter | Strongford | WM | Cadent Gas Limited – DN (WM) | Low | 0.022985 | 0.25 |  |  | 2017-10-11 |  | 2018-04-04 | 2021-01-28 | Invoiced | Closed | 2021-02-24
WM017 | MER/CAD/197/17 | The Turbine meter on MTA was changed out and K-factors in the Omni flow computer were not updated. | Leamington MRA | WM | Cadent Gas Limited – DN | Low | -0.13297 | -1.43 | 2019-01-15 | 2020-09-18 | 2017-10-11 |  | 2019-01-15 | 2022-02-25 | Invoiced | Closed | 2022-02-24
WM018 | MER/CAD/202/20 | It was noticed that there was a period between 11:08 and 12:12 on 9.8.20 where there were high Propane and CV alarms, with the concentration of Propane up to 20%. Whilst the ‘out of spec’ gas was observed no export to grid was taking place. What we have ascertained as part of the initial investigation is there appears to be a metering fault. | Strongford | WM | Cadent Gas Limited – DN (WM) | Low | 0 | 0.233 | 2020-09-30 | 2020-10-22 | 2020-07-28 |  | 2021-11-17 | 2022-05-11 | Invoiced | Closed | Biomethane
WM019 | MER/CAD/203/19 | When the metering system was commissioned, the calibration data entered into the flow computer was that of the atmospheric calibration, as opposed to the high-pressure natural gas calibration, which lead to a previous measurement error (Refer to MER WM015). On 1st September 2015 the high-pressure natural gas calibration data was entered into the flow computer to correct the error, however one calibration point was entered incorrectly. This error was identified during the production of MER WM015 and subsequently corrected on 25th January 2019. | Minworth | WM | Cadent | Low | TBC | TBC | 2015-09-01 | 2018-11-02 | 2014-09-24 | 2014-09-24 | 2015-09-01 | 2021-01-28 | Closed / No Rec Required | Closed
WM020 | MER/CAD/206/21 | Following an Ad hoc activity on site the flow pressure transmitter was left isolated from the metering line as a result of a sticking manifold. | Rugby MTB | WM | Cadent Gas Limited - DN | Low | 0.286 | 3.09 | 2021-03-15 | 2021-04-08 | 2021-03-12 |  | 2021-03-15 | 2022-03-16 | Invoiced | Closed | 2020-09-27
WM021 | MER/CAD/209/21 | An incorrectly calculated fixed factor for carbon dioxide was entered into the flow computer configuration. | Atherstone MRA/MRB Combined | WM | Cadent Gas Limited – DN (WM) | Low | Null | Null | 2021-04-27 | 2021-12-02 | 2021-02-08 |  | 2021-07-02 | 2021-12-02 | Closed / No Rec Required | Closed
WM022 | MER/CAD/210/21 | An incorrectly calculated fixed factor for carbon dioxide was entered into the flow computer configuration. | Leamington MRA/MRB Combined | WM | Cadent Gas Limited – DN | Low | Null | Null | 2021-04-27 | 2021-12-02 | 2021-01-22 |  | 2021-08-06 | 2021-12-02 | Closed / No Rec Required | Closed
WM023 | MER/CAD/213/22 | In 2012 the ultrasonic meters were recalibrated and as a result the k factors in the flow computer were updated with the values from the new calibration certificate. | Lower Quinton UMB | WM | Cadent Gas Limited – DN | Low | 0.025557 | 0.276 | 2021-11-02 | 2022-03-09 | 2012-09-01 | N/A | 2021-11-02 | 2022-05-11 | Invoiced | Closed | 2023-03-24
WM024 | MER/CAD/212/21 | Intermittent erroneous USM flow readings | Barnes Farm | WM | Cadent Gas Limited - DN (WM) | Low | 0 | 0.017 | 2020-12-09 | 2021-09-13 | 2020-08-16 |  | 2021-01-15 | 2021-09-13 | Invoiced | Closed | Biomethane
WM025 | MER/CAD/207/21 | Use of incorrect pressure tapping | Welbeck Colliery | WM | Cadent Gas Limited - DN | Low | 0 | 0.19 | 2021-03-03 | 0 | 2018-04-01 |  | 2021-04-01 | 2022-05-11 | Invoiced | Closed | Biomethane
WM026 | MER/CAD/214/22 | Intermittent flow on USM | Lower Drayton Farm | WM | Cadent Gas Limited – DN (WM) | Low | 2.2e-05 | 0.0002 | 2022-03-31 | 2022-04-01 | 2022-03-08 | N/A | 2022-03-08 | 2022-09-29 | MER Published | Live | Biomethane
WM027 | MER/CAD/238/23 | Disrepency found between metering system and RTU. | Atherstone MRA MRB Combined | WM | Cadent Gas Limited – DN (WM) | not provided | TBC | TBC | 2023-06-08 | 2023-06-08 | TBC |  | TBC | 2023-06-14 | Error Notified | Live
WM028 | MER/CAD/228/22 | Intermittent flow on USM - Propane contamination | Strongford | WM | Cadent | Low | 0.001793 | 0.02 | 2022-09-28 | 2022-09-28 | 2022-05-12 |  | 2022-10-01 | 2023-03-22 | MER Published | Live
WM029 | MER/CAD/230/22 | Intermittent flow on USM | Finham | WM | Cadent | Low | 0.001454 | 0.016 | 2022-12-13 | 2022-12-13 | 2022-12-13 |  | 2023-03-20 | 2023-07-11 | MER Published | Live
WM030 | MER/CAD/227/22 | Intermittent flow on USM - Propane contamination | Brinklow | WM | Cadent | Low | 2e-05 | 0 | 2022-11-29 | 2022-11-29 | 2022-11-25 |  | 2022-11-26 | 2023-03-22 | MER Published | Live
WN002 | MER/WWU/WN002 | Ultrasonic meter from Maelor stream A failed calibration and required repair by manufacturer | Maelor MUA | WN | Wales & West Utilities - DN | Medium | 3.175 | 37.7 | 2016-10-27 | 2017-11-20 | 2014-04-01 |  | 2016-11-16 | 2019-05-13 | Invoiced | Closed | 2019-04-16
WN003 | MER/WWU/WN003 | The two ultrasonic meters at Maelor offtake did not have the meter factors updated after the meters were calibrated. | Maelor MUA | WN | Wales & West Utilities - DN | Low | 1.77 | 19.5 | 2018-09-20 | 2019-05-13 | 2016-10-07 | 2018-10-18 |  | 2020-10-29 | Invoiced | Closed | 2014-07-24
WN004 | MER/WWU/WN004 | Human error led to entering K-Factors and frequencies for both streams into the Omni flow computer incorrectly Compilied meter error calculated at 0.035%, this MER is a Null report. | Maelor MUA | WN | Wales & West Utilities - DN | Low | 0.42 | 8.8 | 2023-04-05 | 2023-06-26 | 2021-03-15 |  | 2023-04-27 | 2023-06-26 | Closed / No Rec Required | Closed
WS001 |  | Intermittent fault with Pressure Transmitter | Gilwern MTA | WS | Wales & West Utilities - DN | High |  | 50.7 | 2008-04-29 | 2009-03-31 | 2007-07-28 |  |  | 2010-09-28 | Invoiced | Closed | 2015-12-29
WS002 | MER/WWU/WS002 | Stream MT1 the pressure and temperature ADC errors were outside the required tolerance. | Gilwern MUA | WS | Wales & West Utilities - DN | Low | 2.4708 | 26.8422 | 2013-10-18 | 2013-12-16 | 2012-05-17 |  | 2013-06-24 | 2014-07-16 | Invoiced | Closed | 2016-06-24
WS003 | MER/WWU/WS003 | Failed validation checks on pressure and temperature ADC's | Dowlais MTA | WS | Wales & West Utilities - DN | Medium | 6.7137 | 35 | 2014-08-08 | 2015-07-17 | 2013-08-19 |  | 2014-07-04 | 2015-12-16 | Invoiced | Closed | 2017-09-26
WS004 | MER/WWU/WS004 | Incorrect K Factors used in flow computer for stream 2 | Dowlais MTB | WS | Wales & West Utilities - DN | Low | 0.9647 | 11 | 2015-11-13 | 2015-12-02 | 2015-08-12 |  | 2015-11-13 | 2016-01-26 | Invoiced | Closed
WS005 | MER/WWU/WS005 | Failed validation checks for pressure ADC on stream 1 and temperature ADC on both streams. Incorrect k-factors in use for stream 2. | Dyffryn Cladach MTA | WS | Wales & West Utilities - DN | Low | 0.78642 | 4.37 | 2015-07-21 | 2015-10-22 | 2014-10-06 |  | 2015-07-21 | 2016-11-22 | Invoiced | Closed
Formulas:
Discovered = '[1]Notification Sheet'!$D16
Error First Notified = '[1]Notification Sheet'!$D17
First Gas Day Where Error Present or; = '[1]Notification Sheet'!$D18
Last Gas Day Where Error Present = '[1]Notification Sheet'!$D20
Latest Notification Update = '[1]Notification Sheet'!$D13

## Status & Validation
Status | Live/Closed | Validation
Error Notified | Live | Live
Awaiting First Available Invoice | Live | Closed
Invoiced | Closed
MER in Compilation | Live
MER Published | Live
No Rec Required | Closed
Passed to NTS | Live
SMER in Compilation | Live
SMER Published | Live

## Offtake Data
Look Up Table For Offtake Data
DN/NTS Offtake Meter(s) | Site Type | Short Code | Upstream Transporter/Supplier | Downstream Transporter | Downstream LDZ | Meter Type
(if applicable)
Aberdeen MTA | Offtake | ABEROF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Adnams | Network Entry | <none> | Adnams Bio Energy Limited | Cadent – DN (EA) | EA | Turbine
Alrewas EM MTD | Offtake | ALREOF | National Grid - NTS | Cadent - DN | EM | Orifice
Alrewas WM MTA | Offtake | ALRWOF | National Grid - NTS | Cadent - DN | WM | Orifice
Alrewas WM MTA/MTB Combined | Offtake | ALRWOF | National Grid - NTS | Cadent - DN | WM | System
Alrewas WM MTB | Offtake | ALRWOF | National Grid - NTS | Cadent - DN | WM | Orifice
Armadale MTA | Offtake | ARMAOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Aspley MTA | Offtake | ASPYOF | National Grid - NTS | Cadent - DN | WM | Orifice
Asselby 38B MRC | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Asselby 38B MRD | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRA | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Asselby 7B MRB | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Ultrasonic
Atherstone MRA | Inter LDZ Transfer | <none> | Cadent – DN (EM) | Cadent – DN (WM) | WM | Turbine
Atherstone MRA/MRB Combined | Inter LDZ Transfer | <none> | Cadent – DN (EM) | Cadent – DN (WM) | WM | System
Atherstone MRB | Inter LDZ Transfer | <none> | Cadent – DN (EM) | Cadent – DN (WM) | WM | Turbine
Audley NW (Crewe) MTC | Offtake | AUDNOF | National Grid - NTS | Cadent - DN | NW | Orifice
Audley WM (Dunkirk) MTD | Offtake | AUDWOF | National Grid - NTS | Cadent - DN | WM | Orifice
Audley WM (Dunkirk) MTD/MTE Combined | Offtake | AUDWOF | National Grid - NTS | Cadent - DN | WM | System
Audley WM (Dunkirk) MTE | Offtake | AUDWOF | National Grid - NTS | Cadent - DN | WM | Orifice
Austrey MTA | Offtake | AUSTOF | National Grid - NTS | Cadent - DN | WM | Orifice
Aylesbeare MUA | Offtake | AYLEOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Aylesbeare MUB | Offtake | AYLEOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Bacton MRD | Offtake | BADSOF | National Grid - NTS | Cadent - DN | EA | Turbine
Baldersby MRA | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Baldersby MRB | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Balgray MTA | Offtake | BALGOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Bathgate UMA | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bathgate UMB | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bishop Aukland MTA | Offtake | BISHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Ultrasonic
Bishop Aukland MTB | Offtake | BISHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Ultrasonic
Blaby MTA | Offtake | BLABOF | National Grid - NTS | Cadent - DN | EM | Orifice
Blackrod MTA | Offtake | BLACOF | National Grid - NTS | Cadent - DN | NW | Orifice
Blackrod MTA/MTB Combined | Offtake | BLACOF | National Grid - NTS | Cadent - DN | NW | System
Blackrod MTB | Offtake | BLACOF | National Grid - NTS | Cadent - DN | NW | Orifice
Blyborough MTA | Offtake | BLYBOF | National Grid - NTS | Cadent - DN | EM | Orifice
Bracknell MTA | Inter LDZ Transfer | <none> | Scotia Gas – DN (SE) | Cadent – DN (NT) | NT | Orifice
Braishfield A MTA | Offtake | BRAAOF | National Grid - NTS | Scotia Gas - DN | SO | USM
Braishfield B MTB | Offtake | BRABOF | National Grid - NTS | Scotia Gas - DN | SO | USM
Bredbury | Network Entry | <none> | Adnams Bio Energy Limited | Cadent – DN (NW) | NW | Rotary Displacement
Brisley MRA | Offtake | BRISOF | National Grid - NTS | Cadent - DN | EA | Turbine
Brisley MRA/MRB Combined | Offtake | BRISOF | National Grid - NTS | Cadent - DN | EA | System
Brisley MRB | Offtake | BRISOF | National Grid - NTS | Cadent - DN | EA | Turbine
Broxburn MTA | Offtake | BROXOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Burley Bank MTA | Offtake | BURLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Burnhervie | Offtake | BURNOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Caldecott MRB | Offtake | CALDOF | National Grid - NTS | Cadent - DN | EM | Turbine
Caldecott MTA | Offtake | CALDOF | National Grid - NTS | Cadent - DN | EM | Orifice
Caldecott MTA/MRB Combined | Offtake | CALDOF | National Grid - NTS | Cadent - DN | EM | System
Careston MRA | Offtake | CAREOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Chittering | Network Entry | <none> | Pretoria Energy Company Limited | Cadent – DN (EA) | EA | Rotary Displacement
Choakford MRA | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Choakford MRB | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Cirencester MRA | Offtake | CIRNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Cirencester MRB | Offtake | CIRNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRB | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRA | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coldstream MTA | Offtake | COLDOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Corbridge MRA | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Ultrasonic
Corbridge MRB | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Ultrasonic
Cowpen Bewley MTA | Offtake | COWPOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Deanshanger | Inter LDZ Transfer | <none> | Scotia Gas – DN (SO) | Cadent – DN (EM) | EM | Turbine
Dowlais MUA | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Dowlais MUB | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Drointon UMA | Offtake | DRTNOF | National Grid - NTS | Cadent - DN | EM | Ultrasonic
Drointon UMA/UMB Combined | Offtake | DRTNOF | National Grid - NTS | Cadent - DN | EM | System
Drointon UMB | Offtake | DRTNOF | National Grid - NTS | Cadent - DN | EM | Ultrasonic
Drum MTA | Offtake | DRUMOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Dryborough Road | Inter LDZ Transfer | <none> | Cadent – DN (NT) | Scotia Gas – DN (SE) | SE | Insertion DP Device
Dunstall Green MRA | Inter LDZ Transfer | <none> | Scotia Gas – DN | Cadent – DN (NT) | NT | Turbine
Dyffryn Cladach MUA | Offtake | DYFNOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Dyffryn Cladach MUB | Offtake | DYFNOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Easton Grey MUA | Offtake | EGRYOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Easton Grey MUB | Offtake | EGRYOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ecclestone MTA | Offtake | ECCLOF | National Grid – NTS | Cadent - DN | NW | Orifice
Elton MTA | Offtake | ELTNOF | National Grid – NTS | Northern Gas Networks – DN | NO | Ultrasonic
Elton MTB | Offtake | ELTNOF | National Grid – NTS | Northern Gas Networks – DN | NO | Ultrasonic
Evesham MTA | Offtake | EVESOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Evesham MTB | Offtake | EVESOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Farningham MTA | Offtake | FARNOF | National Grid – NTS | Scotia Gas – DN | SE | Orifice
Farningham B | Offtake | FARNBOF | National Grid – NTS | Scotia Gas – DN | SE | Ultrasonic
Fiddington MUA | Offtake | FIDDOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Fiddington MUB | Offtake | FIDDOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ganstead MTA | Offtake | GANSOF | National Grid – NTS | Northern Gas Networks – DN | NE | Ultrasonic
Ganstead MTB | Offtake | GANSOF | National Grid – NTS | Northern Gas Networks – DN | NE | Ultrasonic
Gilwern MUA | Offtake | GILWOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Gilwern MUB | Offtake | GILWOF | National Grid - NTS | Wales & West Utilities - DN | WS | Ultrasonic
Glenmavis MTA | Offtake | GLENOF | National Grid – NTS | Scotia Gas – DN | SC | Orifice
Glenmavis MTC | Offtake | GLENOF | National Grid – NTS | Scotia Gas – DN | SC | Orifice
Gosberton MTA | Offtake | GOSBOF | National Grid – NTS | Cadent - DN | EM | Orifice
Great Wilbraham MTA | Offtake | GWILOF | National Grid – NTS | Cadent - DN | EA | Orifice
Guyzance MRA | Offtake | GUYZOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Guyzance MRB | Offtake | GUYZOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Hardwick | Offtake | HARDOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Hibaldstow | Network Entry | <none> | Merlin Nenewables Limited | Cadent – DN (EM) | EM | Rotary Displacement
Hinckley Town | Inter LDZ Transfer | <none> | Cadent – DN (EM) | Cadent – DN (WM) | WM | Insertion Turbine Device
Holkham | Network Entry | <none> | Egmere Energy Ljmited | Cadent – DN (EA) | EA | Rotary Displacement
Holmes Chapel MTA | Offtake | HOLMOF | National Grid – NTS | Cadent - DN | NW | Orifice
Horndon B MTA | Offtake | HORNOF | National Grid – NTS | Cadent - DN | NT | Orifice
Humbleton MRA | Offtake | HUMBOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Humbleton MRB | Offtake | HUMBOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Hume MRA | Offtake | HUMEOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Hume MRB | Offtake | HUMEOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Hydes Pastures MTB | Inter LDZ Transfer | <none> | Cadent – DN (EM) | Cadent – DN (WM) | WM | Orifice
Ilchester MUA | Offtake | ILCHOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ilchester MUB | Offtake | ILCHOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Ipsden MTA | Offtake | IPDNOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Keld MRA | Offtake | KELDOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Kenn MTA | Offtake | KENNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Kenn MTB | Offtake | KENNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Kinknockie MRA | Offtake | KINKOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Kinknockie MRB | Offtake | KINKOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Kirkstead MRA | Offtake | KIRKOF | National Grid – NTS | Cadent - DN | EM | Turbine
Kirkstead MRA/MRB Combined | Offtake | KIRKOF | National Grid – NTS | Cadent - DN | EM | System
Kirkstead MRB | Offtake | KIRKOF | National Grid – NTS | Cadent - DN | EM | Turbine
Langholm MRA | Offtake | LANGOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Leamington MRA | Offtake | LEAMOF | National Grid – NTS | Cadent - DN | WM | Turbine
Leamington MRA/MRB Combined | Offtake | LEAMOF | National Grid – NTS | Cadent - DN | WM | System
Leamington MRB | Offtake | LEAMOF | National Grid – NTS | Cadent - DN | WM | Turbine
Lindholme | Network Entry | <none> | Vulcan Renewables Limited | Cadent – DN (EM) | EM | Rotary Displacement
Little Burdon MTA | Offtake | LBUROF | National Grid – NTS | Northern Gas Networks – DN | NO | Ultrasonic
Little Burdon MTB | Offtake | LBUROF | National Grid – NTS | Northern Gas Networks – DN | NO | Ultrasonic
Littleton Drew MRA | Offtake | LTDWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Lockerbie MTA | Offtake | LOCKOF | National Grid – NTS | Scotia Gas – DN | SC | Orifice
Lower Quinton UMA | Offtake | LOWQOF | National Grid – NTS | Cadent - DN | WM | Ultrasonic
Lower Quinton UMA/UMB Combined | Offtake | LOWQOF | National Grid – NTS | Cadent - DN | WM | System
Lower Quinton UMB | Offtake | LOWQOF | National Grid – NTS | Cadent - DN | WM | Ultrasonic
Lupton MTA | Offtake | LUPTOF | National Grid – NTS | Cadent - DN | NW | Orifice
Luxborough Lane MTA | Offtake | LUXBOF | National Grid – NTS | Cadent - DN | NT | Orifice
Luxborough Lane MTA/MTB Combined | Offtake | LUXBOF | National Grid – NTS | Cadent - DN | NT | System
Luxborough Lane MTB | Offtake | LUXBOF | National Grid – NTS | Cadent - DN | NT | Orifice
Maelor MUA | Offtake | MAELOF | National Grid - NTS | Wales & West Utilities - DN | WN | Ultrasonic
Maelor MUB | Offtake | MAELOF | National Grid - NTS | Wales & West Utilities - DN | WN | Ultrasonic
Malpas MRA | Offtake | MALPOF | National Grid – NTS | Cadent - DN | NW | Turbine
Mappowder MTA | Offtake | MAPPOF | National Grid – NTS | Scotia Gas – DN | SO | Orifice
Market Harborough MTA | Offtake | MKHBOF | National Grid – NTS | Cadent - DN | EM | Orifice
Martyr's Lane (Blackmore Crescent) | Inter LDZ Transfer | <none> | Scotia Gas – DN (SE) | Cadent – DN (NT) | NT | Insertion DP Device
Matching Green MTA | Offtake | MTCHOF | National Grid – NTS | Cadent - DN | EA | Orifice
Melkinthorpe MRA | Offtake | MELKOF | National Grid – NTS | Northern Gas Networks – DN | NO | Turbine
Mickle Trafford MTA | Offtake | MICKOF | National Grid – NTS | Cadent - DN | NW | Orifice
Milwich MTA | Offtake | MILWOF | National Grid – NTS | Cadent - DN | WM | Orifice
Minworth | Network Entry | <none> | Severn Trent Water Limited | Cadent – DN (WM) | WM | Rotary Displacement
Nether Howcleugh MRA | Offtake | NETHOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Nether Howcleugh MRB | Offtake | NETHOF | National Grid – NTS | Scotia Gas – DN | SC | Turbine
Oak Avenue | Inter LDZ Transfer | <none> | Cadent – DN (NT) | Scotia Gas – DN (SE) | SE | Insertion DP Device
Pannal MTA | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Pannal MTB | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Partington MTA | Offtake | PART OF | National Grid - NTS | Cadent - DN | NW | Orifice
Paull MTA | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Paull MTB | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Peterborough Eye MTA | Offtake | PEYEOF | National Grid - NTS | Cadent - DN | EA | Orifice
Peterborough Eye MTA/MTB Combined | Offtake | PEYEOF | National Grid - NTS | Cadent - DN | EA | System
Peterborough Eye MTB | Offtake | PEYEOF | National Grid - NTS | Cadent - DN | EA | Orifice
Peters Green 1 MTA | Offtake | PGRNOF | National Grid - NTS | Cadent - DN | NT | Orifice
Peters Green 1 MTA/MTB Combined | Offtake | PGRNOF | National Grid - NTS | Cadent - DN | NT | System
Peters Green 1 MTB | Offtake | PGRNOF | National Grid - NTS | Cadent - DN | NT | Orifice
Peters Green 2 (South Mimms) MTC | Offtake | PGSMOF | National Grid - NTS | Cadent - DN | NT | Orifice
Peters Green 2 (South Mimms) MTC/MTD Combined | Offtake | PGSMOF | National Grid - NTS | Cadent - DN | NT | System
Peters Green 2 (South Mimms) MTD | Offtake | PGSMOF | National Grid - NTS | Cadent - DN | NT | Orifice
Pickering MTA | Offtake | PICKOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Pitcairngreen MRA | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pitcairngreen MRB | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Portsdown Hill | Entry Point | None |  | Scotia Gas - DN | SO | Turbine
Poundbury | Entry Point | None |  | Scotia Gas - DN | SO | Turbine
Pucklechurch MTA | Offtake | PUCKOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Pucklechurch MTB | Offtake | PUCKOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Rawcliffe MRA | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Rawcliffe MRB | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Roehampton Lane | Inter LDZ Transfer | <none> | Scotia Gas – DN (SE) | Cadent – DN (NT) | NT | Insertion DP Device
Ross WM MTA | Offtake | ROSSOF | National Grid - NTS | Cadent - DN | WM | Orifice
Ross-On-Wye MRA | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Ross-On-Wye MRB | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Roudham Heath MTA | Offtake | ROUDOF | National Grid - NTS | Cadent - DN | EA | Orifice
Royston MRA | Offtake | ROYSOF | National Grid - NTS | Cadent - DN | EA | Turbine
Royston MRA/MRB Combined | Offtake | ROYSOF | National Grid - NTS | Cadent - DN | EA | System
Royston MRB | Offtake | ROYSOF | National Grid - NTS | Cadent - DN | EA | Turbine
Rugby MTB | Offtake | RUGBOF | National Grid - NTS | Cadent - DN | WM | Orifice
Saltwick 1 | Offtake | SALTOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Samlesbury MTA | Offtake | SAMLOF | National Grid - NTS | Cadent - DN | NW | Orifice
Scampton | Network Entry | <none> | Grange Farm Energy Limited | Cadent – DN (EM) | EM | Rotary Displacement
Seabank MUA | Offtake | SEABOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Seabank MUB | Offtake | SEABOF | National Grid - NTS | Wales & West Utilities - DN | SW | Ultrasonic
Shorne MTA | Offtake | SHOROF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Shustoke MTA | Offtake | SHUSOF | National Grid - NTS | Cadent - DN | WM | Orifice
Silk Willoughby MRA | Offtake | SILKOF | National Grid - NTS | Cadent - DN | EM | Turbine
Silk Willoughby MRA/MRB Combined | Offtake | SILKOF | National Grid - NTS | Cadent - DN | EM | System
Silk Willoughby MRB | Offtake | SILKOF | National Grid - NTS | Cadent - DN | EM | Turbine
Sotterley | Network Entry | <none> | Biocore AD2 Limited | Cadent – DN (EA) | EA | Rotary Displacement
Soutra MTA | Offtake | SOUTOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
St Fergus MTA | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
St Fergus MTB | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRA | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRB | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stratford MRA | Offtake | STRAOF | National Grid - NTS | Cadent - DN | WM | Turbine
Stratford MRB | Offtake | STRAOF | National Grid - NTS | Cadent - DN | WM | Turbine
Sutton Bridge MRA | Offtake | SUTNOF | National Grid - NTS | Cadent - DN | EM | Turbine
Sutton Bridge MRA/MRB Combined | Offtake | SUTNOF | National Grid - NTS | Cadent - DN | EM | System
Sutton Bridge MRB | Offtake | SUTNOF | National Grid - NTS | Cadent - DN | EM | Turbine
Tatsfield MTA | Offtake | TATSOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Thornton Curtis MTA | Offtake | CURTOF | National Grid - NTS | Cadent - DN | EM | Orifice
Thrintoft MTA | Offtake | THRNOF | National Grid - NTS | Northern Gas Networks - DN | NO | Ultrasonic
Thrintoft MTB | Offtake | THRNOF | National Grid - NTS | Northern Gas Networks - DN | NO | Ultrasonic
Tow Law MRA | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Tow Law MRB | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Towton MTA | Offtake | TOWTOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Towton MTB | Offtake | TOWTOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Tur Langton MTA | Offtake | TURLOF | National Grid - NTS | Cadent - DN | EM | Orifice
Walesby MRA | Offtake | WSBYOF | National Grid - NTS | Cadent - DN | EM | Turbine
Walesby MRA/MRB Combined | Offtake | WSBYOF | National Grid - NTS | Cadent - DN | EM | System
Walesby MRB | Offtake | WSBYOF | National Grid - NTS | Cadent - DN | EM | Turbine
Warburton MTA | Offtake | WARBOF | National Grid - NTS | Cadent - DN | NW | Orifice
West Winch MTA | Offtake | WINCOF | National Grid - NTS | Cadent - DN | EA | Orifice
Weston Point MTB | Offtake | WESTOF | National Grid - NTS | Cadent - DN | NW | Orifice
Wetheral MTA | Offtake | WETHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Ultrasonic
Wetheral MTB | Offtake | WETHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Ultrasonic
Whitwell MTA | Offtake | WHITOF | National Grid - NTS | Cadent - DN | EA | Orifice
Whitwell MTA/MTB Combined | Offtake | WHITOF | National Grid - NTS | Cadent - DN | EA | System
Whitwell MTB | Offtake | WHITOF | National Grid - NTS | Cadent - DN | EA | Orifice
Widnes | Network Entry | <none> | Refood UK Limited | Cadent – DN (NW) | NW | Rotary Displacement
Winkfield 2 MTB | Offtake | WNKSOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Winkfield MTA | Offtake | WINKOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Winkfield NT MTC | Offtake | WINTOF | National Grid - NTS | Cadent - DN | NT | Orifice
Wytch Farm | Network Entry | <none> | Perenco | Scotia Gas - DN | SO | Orifice
Yelverton MTA | Offtake | YELVOF | National Grid - NTS | Cadent - DN | EA | Orifice
| Over/Under Indicator | Error Magnitude |  | Error Status
| Over | High | >= 50 GWh | Error Notified
| Under | Low | < 30 GWh | MER in Compilation
|  | Medium | >= 30, < 50 GWh | SMER in Compilation
MER Published
SMER Published
Awaiting First Available Invoice
Invoiced
Closed / No Rec Required