## Slide 1: NTS Specification for Mercury
Transmission Workgroup
October 2023
National Gas Transmission |

## Slide 2: Decision
Thank you for your input regarding the NTS specification for Mercury
After considering all the information available to us, we have determined to leave the guidance limit for mercury at 10µg/m3 at this time, as detailed in the Gas Ten Year Statement.
The Gas Ten Year Statement can be found on our website: https://www.nationalgas.com/insight-and-innovation/gas-ten-year-statement-gtys

## Slide 3: Background
Mercury is not directly stated in GS(M)R but is covered indirectly in that the gas we transport “shall not contain solid or liquid material which may interfere with the integrity or operation of pipes or any gas appliance”.
We do not measure or monitor mercury levels on the NTS
Guidance Limit was included in 2020 due to queries received as to what a ‘negligible’ level was and what we would accept on the NTS:
    10µg/m3 is typically specified for heat exchangers in industrial and power plant
    Therefore the guidance limit was set at 10µg/m3 and published in the GTYS as a means to capture and share with industry
  We received an enquiry from an upstream operator if we would accept mercury levels above the maximum GTYS guidance limit of 10μg/m3, possibly up to 20μg/m3

## Slide 4: Background Cont.
  A short survey was carried out with industry last year. We asked whether mercury content in natural gas presents any risks and the impact of increasing the limit would have on customers’ operations
      Survey results indicated a mixed response, confusion around the limit, and concerns around safety and equipment at the current level
  Sampling undertaken in 2022:
  Further survey was carried out May 2023 to determine what impact lowering the mercury guidance limit would have on customers’ operations
      Survey results indicated a clear divide
Points Sampled | Location | Result
23 | Easington/Bacton/St. Fergus/Teesside/Lupton/Newton Noyes | <0.1µg/m3

## Slide 5: Survey Results
Environmental Poison and as such an unwanted component
Power reporting assumption
Concerns regarding equipment at current level
Strategic long-term decisions have been made based on the current limits
Potentially unattractive for new fields
If mercury limit were to reduce, this would potentially increase costs
Greater clarity around current limit and background
Requests for Mercury monitoring on the NTS and regular reporting
Key themes
Support of a reduction
Support to remain as-is

## Slide 6: Rationale for Decision
The guidance level of 10µ/m3 meets our obligations in terms of GS(M)R - the gas we transport “shall not contain solid or liquid material which may interfere with the integrity or operation of pipes or any gas appliance”
    We consider this to be a safe level in terms of metal networks and combustion components
    Consistent with mercury limit in DNs
Security of Supply
Currently, we do not have mercury monitoring equipment, so compliance is not measurable

## Slide 7: Future Developments
Further Sampling. Further sampling (to include mercury) is scheduled to take place on the NTS over Winter 23
Risk Assessment. We are currently in the process of running a risk assessment via a 3rd party to explore what additional components there may be value in monitoring
    (This could include mercury, radioactive material and benzene for example)
Device Trials. Following the risk assessment, a desk-top exercise may be carried out to look at appropriate equipment which could provide live measurement readings (which may include mercury). This will be followed by device trials.
RIIO3. If the business decides to go-ahead, we will request funds in RIIO3. Installation would happen at key points on the network, in phases, between 2027-31
A further update on the above can be provided early next year