## Notification Sheet
Measurement Error Notification
Unique Reference Number (Allocated by Joint Office) |  | NO005
Error Status | Error Notified
Brief Description | Low DP Cell found out of tolerance
Reason Measurement Error Detected | Review of last years validation results
Process Dates | Latest Notification Update | 2010-06-11
| Anticipated MER/SMER Publication | 2010-07-10
Measurement Error Dates | First Notified | 2010-06-11
| Discovered | 2010-01-20
| Started (or last good read) | 2008-05-15
| Corrected | 2009-05-13
Offtake |  | Elton MTA | ELTNOF
Transporter | Upstream | National Grid - NTS
| Downstream | Northern Gas Networks - DN
Meter Type |  | Orifice
LDZ |  | NO
Average flow rates for the meter for the perceived duration of the Measurement Error (MCM/Day) |  | 1.539
Assessed volume of error (MCM) |  | 0.7218
Estimated quantity of error (GWh) |  | 8.203
Estimated Significance |  | Low | < 30 GWh
Systematic Bias? |  | Yes
Over or Under Read? |  | Over

## Look Up Data
Look Up Table For Offtake Data
DN/NTS Offtake Meter | Site Type | Short Code | Upstream Transporter | Downstream Transporter | LDZ | Meter Type
Aberdeen MTA | Offtake | ABEROF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Alrewas EM MTD | Offtake | ALREOF | National Grid - NTS | National Grid - DN | EM | Orifice
Alrewas WM MTA | Offtake | ALRWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Alrewas WM MTB | Offtake | ALRWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Armadale MTA | Offtake | ARMAOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Aspley MTA | Offtake | ASPYOF | National Grid - NTS | National Grid - DN | WM | Orifice
Asselby 38B MRC | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Asselby 38B MRD | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRA | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRB | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Atherstone MRA | Inter LDZ Offtake | <none> | National Grid - DN | National Grid - DN | WM | Turbine
Atherstone MRB | Inter LDZ Offtake | <none> | National Grid - DN | National Grid - DN | WM | Turbine
Audley (Crewe) MTC | Offtake | AUDNOF | National Grid - NTS | National Grid - DN | NW | Orifice
Audley (Dunkirk) MTD | Offtake | AUDWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Audley (Dunkirk) MTE | Offtake | AUDWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Austrey MTA | Offtake | AUSTOF | National Grid - NTS | National Grid - DN | WM | Orifice
Aylesbeare MTA | Offtake | AYLEOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Bacton MRD | Offtake | BADSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Baldersby MRA | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Baldersby MRB | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Balgray MTA | Offtake | BALGOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Bathgate UMA | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bathgate UMB | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bishop Aukland MTA | Offtake | BISHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Blaby MTA | Offtake | BLABOF | National Grid - NTS | National Grid - DN | EM | Orifice
Blackrod MTA | Offtake | BLACOF | National Grid - NTS | National Grid - DN | NW | Orifice
Blackrod MTB | Offtake | BLACOF | National Grid - NTS | National Grid - DN | NW | Orifice
Blyborough MTA | Offtake | BLYBOF | National Grid - NTS | National Grid - DN | EM | Orifice
Bracknell MTA | Inter LDZ Offtake | <none> | Scotia Gas - DN | National Grid - DN | NT | Orifice
Braishfield A MTA | Offtake | BRAAOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Braishfield B MTB | Offtake | BRABOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Brisley MRA | Offtake | BRISOF | National Grid - NTS | National Grid - DN | EA | Turbine
Brisley MRB | Offtake | BRISOF | National Grid - NTS | National Grid - DN | EA | Turbine
Broxburn MTA | Offtake | BROXOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Burley Bank MTA | Offtake | BURLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Caldecott MRB | Offtake | CALDOF | National Grid - NTS | National Grid - DN | EM | Turbine
Caldecott MTA | Offtake | CALDOF | National Grid - NTS | National Grid - DN | EM | Orifice
Careston MRA | Offtake | CAREOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Choakford MRA | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Choakford MRB | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Cirencester MRB | Offtake | CIRNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRB | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRA | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coldstream MTA | Offtake | COLDOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Corbridge MRA | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Corbridge MRB | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Cowpen Bewley MTA | Offtake | COWPOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Dowlais MTA | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Dowlais MTB | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Drointon UMA | Offtake | DRTNOF | National Grid - NTS | National Grid - DN | EM | Ultrasonic
Drointon UMB | Offtake | DRTNOF | National Grid - NTS | National Grid - DN | EM | Ultrasonic
Drum MTA | Offtake | DRUMOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Dunstall Green MRA | Inter LDZ Offtake | <none> | Scotia Gas - DN | National Grid - DN | NT | Turbine
Dyffryn Cladach MTA | Offtake | DYFNOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Easton Grey MTA | Offtake | EGRYOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Ecclestone MTA | Offtake | ECCLOF | National Grid - NTS | National Grid - DN | NW | Orifice
Elton MTA | Offtake | ELTNOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Evesham MTA | Offtake | EVESOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Evesham MTB | Offtake | EVESOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Farningham MTA | Offtake | FARNOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Fiddington MTA | Offtake | FIDDOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Ganstead MTA | Offtake | GANSOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Gilwern MTA | Offtake | GILWOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Glenmavis MTA | Offtake | GLENOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Glenmavis MTC | Offtake | GLENOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Gosberton MTA | Offtake | GOSBOF | National Grid - NTS | National Grid - DN | EM | Orifice
Great Wilbraham MTA | Offtake | GWILOF | National Grid - NTS | National Grid - DN | EA | Orifice
Guyzance MRA | Offtake | GUYZOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Guyzance MRB | Offtake | GUYZOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Hardwick | Offtake | HARDOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Holmes Chapel MTA | Offtake | HOLMOF | National Grid - NTS | National Grid - DN | NW | Orifice
Horndon B MTA | Offtake | HORNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Humbleton MRA | Offtake | HUMBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Humbleton MRB | Offtake | HUMBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Hume MRA | Offtake | HUMEOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Hume MRB | Offtake | HUMEOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Hydes Pastures MTA | Inter LDZ Offtake | <none> | National Grid - DN | National Grid - DN | WM | Orifice
Ilchester MTA | Offtake | ILCHOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Ipsden MTA | Offtake | IPDNOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Keld MRA | Offtake | KELDOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Kenn MTA | Offtake | KENNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Kenn MTB | Offtake | KENNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Kinknockie MRA | Offtake | KINKOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Kinknockie MRB | Offtake | KINKOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Kirkstead MRB | Offtake | KIRKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Kirkstead MTA | Offtake | KIRKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Langholm MRA | Offtake | LANGOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Leamington MRA | Offtake | LEAMOF | National Grid - NTS | National Grid - DN | WM | Turbine
Leamington MRB | Offtake | LEAMOF | National Grid - NTS | National Grid - DN | WM | Turbine
Little Burdon MTA | Offtake | LBUROF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Littleton Drew MRA | Offtake | LTDWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Lockerbie MTA | Offtake | LOCKOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Lower Quinton UMA | Offtake | LOWQOF | National Grid - NTS | National Grid - DN | WM | Ultrasonic
Lower Quinton UMB | Offtake | LOWQOF | National Grid - NTS | National Grid - DN | WM | Ultrasonic
Lupton MTA | Offtake | LUPTOF | National Grid - NTS | National Grid - DN | NW | Orifice
Luxborough Lane MTA | Offtake | LUXBOF | National Grid - NTS | National Grid - DN | NT | Orifice
Luxborough Lane MTB | Offtake | LUXBOF | National Grid - NTS | National Grid - DN | NT | Orifice
Maelor MTA | Offtake | MAELOF | National Grid - NTS | Wales & West Utilities - DN | WN | Orifice
Maelor MTB | Offtake | MAELOF | National Grid - NTS | Wales & West Utilities - DN | WN | Turbine
Malpas MRA | Offtake | MALPOF | National Grid - NTS | National Grid - DN | NW | Turbine
Mappowder MTA | Offtake | MAPPOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Market Harborough MTA | Offtake | MKHBOF | National Grid - NTS | National Grid - DN | EM | Orifice
Matching Green MTA | Offtake | MTCHOF | National Grid - NTS | National Grid - DN | EA | Orifice
Matching Green MTB | Offtake | MTCHOF | National Grid - NTS | National Grid - DN | EA | Orifice
Melkinthorpe MRA | Offtake | MELKOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Mickle Trafford MTA | Offtake | MICKOF | National Grid - NTS | National Grid - DN | NW | Orifice
Milwich MTA | Offtake | MILWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Nether Howcleugh MRA | Offtake | NETHOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Nether Howcleugh MRB | Offtake | NETHOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pannal MTA | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Pannal MTB | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Partington MTA | Offtake | PART OF | National Grid - NTS | National Grid - DN | NW | Orifice
Paull MTA | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Paull MTB | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Peterborough Eye MTA | Offtake | PEYEOF | National Grid - NTS | National Grid - DN | EA | Orifice
Peterborough Eye MTB | Offtake | PEYEOF | National Grid - NTS | National Grid - DN | EA | Orifice
Peters Green 2 (South Mimms) MTC | Offtake | PGSMOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green 2 (South Mimms) MTD | Offtake | PGSMOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green MTA | Offtake | PGRNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green MTB | Offtake | PGRNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Pickering MTA | Offtake | PICKOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Pitcairngreen MRA | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pitcairngreen MRB | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pucklechurch MTA | Offtake | PUCKOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Rawcliffe MRA | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Rawcliffe MRB | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Ross WM MTA | Offtake | ROSSOF | National Grid - NTS | National Grid - DN | WM | Orifice
Ross-On-Wye MRA | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Ross-On-Wye MRB | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Roudham Heath MTA | Offtake | ROUDOF | National Grid - NTS | National Grid - DN | EA | Orifice
Royston MRA | Offtake | ROYSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Royston MRB | Offtake | ROYSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Rugby MTA | Offtake | RUGBOF | National Grid - NTS | National Grid - DN | WM | Orifice
Saltwick 1 | Offtake | SALTOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Samlesbury MTA | Offtake | SAMLOF | National Grid - NTS | National Grid - DN | NW | Orifice
Seabank MTA | Offtake | SEABOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Shorne MTA | Offtake | SHOROF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Shustoke MTA | Offtake | SHUSOF | National Grid - NTS | National Grid - DN | WM | Orifice
Silk Willoughby MRA | Offtake | SILKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Silk Willoughby MRB | Offtake | SILKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Soutra MTA | Offtake | SOUTOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
St Fergus MTA | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
St Fergus MTB | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRA | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRB | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stratford MRA | Offtake | STRAOF | National Grid - NTS | National Grid - DN | WM | Turbine
Stratford MRB | Offtake | STRAOF | National Grid - NTS | National Grid - DN | WM | Turbine
Sutton Bridge MRA | Offtake | SUTNOF | National Grid - NTS | National Grid - DN | EM | Turbine
Sutton Bridge MRB | Offtake | SUTNOF | National Grid - NTS | National Grid - DN | EM | Turbine
Tatsfield MTA | Offtake | TATSOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Thornton Curtis MTA | Offtake | CURTOF | National Grid - NTS | National Grid - DN | EM | Orifice
Thrintoft MTA | Offtake | THRNOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Tow Law MRA | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Tow Law MRB | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Towton MTA | Offtake | TOWTOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Tur Langton MTA | Offtake | TURLOF | National Grid - NTS | National Grid - DN | EM | Orifice
Walesby MRA | Offtake | WSBYOF | National Grid - NTS | National Grid - DN | EM | Turbine
Walesby MRB | Offtake | WSBYOF | National Grid - NTS | National Grid - DN | EM | Turbine
Warburton MTA | Offtake | WARBOF | National Grid - NTS | National Grid - DN | NW | Orifice
West Winch MTA | Offtake | WINCOF | National Grid - NTS | National Grid - DN | EA | Orifice
Weston Point MTB | Offtake | WESTOF | National Grid - NTS | National Grid - DN | NW | Orifice
Wetheral MTA | Offtake | WETHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Whitwell MTA | Offtake | WHITOF | National Grid - NTS | National Grid - DN | EA | Orifice
Whitwell MTB | Offtake | WHITOF | National Grid - NTS | National Grid - DN | EA | Orifice
Winkfield 2 MTB | Offtake | WNKSOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Winkfield MTA | Offtake | WINKOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Winkfield NT MTC | Offtake | WINTOF | National Grid - NTS | National Grid - DN | NT | Orifice
Yelverton MTB | Offtake | YELVOF | National Grid - NTS | National Grid - DN | EA | Orifice
Systematic Bias | Over/Under Indicator | Error Magnitude |  | Error Status
Yes | Over | High | >= 50 GWh | Error Notified
No | Under | Low | < 30 GWh | MER in Compilation
|  | Medium | >= 30, < 50 GWh | SMER in Compilation
MER Published
SMER Published
Awaiting First Available Invoice
Invoiced
Closed / No Rec Required

## Extract for JO Database
Report ID | Ref | Description | Reason | Latest Update | Anticipated Production | First Notified | Discovered | Started | Corrected | Offtake | Av Flow Rates | Volume | Quantity | Significance | Bias | Over/Under | Error Status
NO00511062010 | NO005 | Low DP Cell found out of tolerance | Review of last years validation results | 2010-06-11 | 2010-07-10 | 2010-06-11 | 2010-01-20 | 39583 | 39946 | Elton MTA | 1.539 | 0.7218 | 8.203 | Low | Yes | Over | Error Notified