## Notification Sheet
Measurement Error Notification
Unique Reference Number (Allocated by Joint Office) |  | WM014
DN Reference | MER/UKD/182/13
Error Status | MER in Compilation
Brief Description | Incorrect flow computer firmware was used.
Reason Measurement Error Detected | The Senior Network Technician at site reported a difficulty with the CP1 test during the T/PR/ME/2 parts 1-3 validation process. Together with the site Network Technician, the Measurement and Process Group investigated the issue and determined that the Compression Factor was not being calculated correctly. Further information: http://www.gasgovernance.co.uk/oa/260313 (08 April 2013 WM014 – Atherstone MRA Presentation - provided by National Grid).
Process Dates | Latest Notification Update | 2013-02-22 | dd/mm/yyyy
| Anticipated MER/SMER Publication |  | dd/mm/yyyy
Measurement Error Dates | Discovered | 2013-02-20 | dd/mm/yyyy
| First Notified | 2013-02-21 | dd/mm/yyyy
| First Gas Day Where Error Present | 2012-03-14 | dd/mm/yyyy
| Last Gas Day Where Error Present | 2013-02-20 | dd/mm/yyyy
Offtake |  | Atherstone MRA | <none>
Transporter | Upstream | National Grid - DN
| Downstream | National Grid - DN
Meter Type |  | Turbine
LDZ |  | WM
Average flow rates for the meter for the perceived duration of the Measurement Error (MCM/Day) |  | N/A | MCM/Day
Declared volume of error (MCM) |  | 12.11 | MCM
Estimated quantity of error (GWh) |  | 131.9 | GWh
Estimated Significance |  | High | >= 50 GWh
Over or Under Read? |  | Over
MCM = million cubic meters
Unless stated otherwise all volumes are for the real dry gas at ISO Standard Reference conditions of 15°C and 1.01325 bar.
Unless stated otherwise all energies are calculated using a gross calorific value for the real dry gas at ISO reference conditions of 15°C (combustion) and 15°C and 1.01325 bar (metering).

## Look Up Data
Look Up Table For Offtake Data
DN/NTS Offtake Meter | Site Type | Short Code | Upstream Transporter | Downstream Transporter | LDZ | Meter Type
Aberdeen MTA | Offtake | ABEROF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Alrewas EM MTD | Offtake | ALREOF | National Grid - NTS | National Grid - DN | EM | Orifice
Alrewas WM MTA | Offtake | ALRWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Alrewas WM MTB | Offtake | ALRWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Alrewas WM MTA/MTB Combined | Offtake | ALRWOF | National Grid - NTS | National Grid - DN | WM | System
Armadale MTA | Offtake | ARMAOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Aspley MTA | Offtake | ASPYOF | National Grid - NTS | National Grid - DN | WM | Orifice
Asselby 38B MRC | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Asselby 38B MRD | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRA | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Asselby 7B MRB | Offtake | ASSLOF | National Grid - NTS | Northern Gas Networks – DN | NE | Turbine
Atherstone MRA | Inter LDZ Transfer | <none> | National Grid - DN | National Grid - DN | WM | Turbine
Atherstone MRB | Inter LDZ Transfer | <none> | National Grid - DN | National Grid - DN | WM | Turbine
Atherstone MRA/MRB Combined | Inter LDZ Transfer | <none> | National Grid - DN | National Grid - DN | WM | System
Audley NW (Crewe) MTC | Offtake | AUDNOF | National Grid - NTS | National Grid - DN | NW | Orifice
Audley WM (Dunkirk) MTD | Offtake | AUDWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Audley WM (Dunkirk) MTE | Offtake | AUDWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Audley WM (Dunkirk) MTD/MTE Combined | Offtake | AUDWOF | National Grid - NTS | National Grid - DN | WM | System
Austrey MTA | Offtake | AUSTOF | National Grid - NTS | National Grid - DN | WM | Orifice
Aylesbeare MTA | Offtake | AYLEOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Bacton MRD | Offtake | BADSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Baldersby MRA | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Baldersby MRB | Offtake | BALDOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Balgray MTA | Offtake | BALGOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Bathgate UMA | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bathgate UMB | Offtake | BATHOF | National Grid - NTS | Scotia Gas - DN | SC | Ultrasonic
Bishop Aukland MTA | Offtake | BISHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Blaby MTA | Offtake | BLABOF | National Grid - NTS | National Grid - DN | EM | Orifice
Blackrod MTA | Offtake | BLACOF | National Grid - NTS | National Grid - DN | NW | Orifice
Blackrod MTB | Offtake | BLACOF | National Grid - NTS | National Grid - DN | NW | Orifice
Blackrod MTA/MTB Combined | Offtake | BLACOF | National Grid - NTS | National Grid - DN | NW | System
Blyborough MTA | Offtake | BLYBOF | National Grid - NTS | National Grid - DN | EM | Orifice
Bracknell MTA | Inter LDZ Transfer | <none> | Scotia Gas - DN | National Grid - DN | NT | Orifice
Braishfield A MTA | Offtake | BRAAOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Braishfield B MTB | Offtake | BRABOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Brisley MRA | Offtake | BRISOF | National Grid - NTS | National Grid - DN | EA | Turbine
Brisley MRB | Offtake | BRISOF | National Grid - NTS | National Grid - DN | EA | Turbine
Brisley MRA/MRB Combined | Offtake | BRISOF | National Grid - NTS | National Grid - DN | EA | System
Broxburn MTA | Offtake | BROXOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Burley Bank MTA | Offtake | BURLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Caldecott MTA | Offtake | CALDOF | National Grid - NTS | National Grid - DN | EM | Orifice
Caldecott MRB | Offtake | CALDOF | National Grid - NTS | National Grid - DN | EM | Turbine
Caldecott MTA/MRB Combined | Offtake | CALDOF | National Grid - NTS | National Grid - DN | EM | System
Careston MRA | Offtake | CAREOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Choakford MRA | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Choakford MRB | Offtake | CHOAOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Cirencester MRB | Offtake | CIRNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRB | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coffinswell MRA | Offtake | COFFOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Coldstream MTA | Offtake | COLDOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Corbridge MRA | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Corbridge MRB | Offtake | CORBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Cowpen Bewley MTA | Offtake | COWPOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Dowlais MTA | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Dowlais MTB | Offtake | DOWLOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Drointon UMA | Offtake | DRTNOF | National Grid - NTS | National Grid - DN | EM | Ultrasonic
Drointon UMB | Offtake | DRTNOF | National Grid - NTS | National Grid - DN | EM | Ultrasonic
Drointon UMA/UMB Combined | Offtake | DRTNOF | National Grid - NTS | National Grid - DN | EM | System
Drum MTA | Offtake | DRUMOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Dunstall Green MRA | Inter LDZ Transfer | <none> | Scotia Gas - DN | National Grid - DN | NT | Turbine
Dyffryn Cladach MTA | Offtake | DYFNOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Easton Grey MTA | Offtake | EGRYOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Ecclestone MTA | Offtake | ECCLOF | National Grid - NTS | National Grid - DN | NW | Orifice
Elton MTA | Offtake | ELTNOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Evesham MTA | Offtake | EVESOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Evesham MTB | Offtake | EVESOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Farningham MTA | Offtake | FARNOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Fiddington MTA | Offtake | FIDDOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Ganstead MTA | Offtake | GANSOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Gilwern MTA | Offtake | GILWOF | National Grid - NTS | Wales & West Utilities - DN | WS | Orifice
Glenmavis MTA | Offtake | GLENOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Glenmavis MTC | Offtake | GLENOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Gosberton MTA | Offtake | GOSBOF | National Grid - NTS | National Grid - DN | EM | Orifice
Great Wilbraham MTA | Offtake | GWILOF | National Grid - NTS | National Grid - DN | EA | Orifice
Guyzance MRA | Offtake | GUYZOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Guyzance MRB | Offtake | GUYZOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Hardwick | Offtake | HARDOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Holmes Chapel MTA | Offtake | HOLMOF | National Grid - NTS | National Grid - DN | NW | Orifice
Horndon B MTA | Offtake | HORNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Humbleton MRA | Offtake | HUMBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Humbleton MRB | Offtake | HUMBOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Hume MRA | Offtake | HUMEOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Hume MRB | Offtake | HUMEOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Hydes Pastures MTA | Inter LDZ Transfer | <none> | National Grid - DN | National Grid - DN | WM | Orifice
Ilchester MTA | Offtake | ILCHOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Ipsden MTA | Offtake | IPDNOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Ipsden MTC | Offtake | IPDBOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Keld MRA | Offtake | KELDOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Kenn MTA | Offtake | KENNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Kenn MTB | Offtake | KENNOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Kinknockie MRA | Offtake | KINKOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Kinknockie MRB | Offtake | KINKOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Kirkstead MRB | Offtake | KIRKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Kirkstead MRA | Offtake | KIRKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Kirkstead MRA/MRB Combined | Offtake | KIRKOF | National Grid - NTS | National Grid - DN | EM | System
Langholm MRA | Offtake | LANGOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Leamington MRA | Offtake | LEAMOF | National Grid - NTS | National Grid - DN | WM | Turbine
Leamington MRB | Offtake | LEAMOF | National Grid - NTS | National Grid - DN | WM | Turbine
Leamington MRA/MRB Combined | Offtake | LEAMOF | National Grid - NTS | National Grid - DN | WM | System
Little Burdon MTA | Offtake | LBUROF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Littleton Drew MRA | Offtake | LTDWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Lockerbie MTA | Offtake | LOCKOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
Lower Quinton UMA | Offtake | LOWQOF | National Grid - NTS | National Grid - DN | WM | Ultrasonic
Lower Quinton UMB | Offtake | LOWQOF | National Grid - NTS | National Grid - DN | WM | Ultrasonic
Lower Quinton UMA/UMB Combined | Offtake | LOWQOF | National Grid - NTS | National Grid - DN | WM | System
Lupton MTA | Offtake | LUPTOF | National Grid - NTS | National Grid - DN | NW | Orifice
Luxborough Lane MTA | Offtake | LUXBOF | National Grid - NTS | National Grid - DN | NT | Orifice
Luxborough Lane MTB | Offtake | LUXBOF | National Grid - NTS | National Grid - DN | NT | Orifice
Luxborough Lane MTA/MTB Combined | Offtake | LUXBOF | National Grid - NTS | National Grid - DN | NT | System
Maelor MUA | Offtake | MAELOF | National Grid - NTS | Wales & West Utilities - DN | WN | Ultrasonic
Maelor MUB | Offtake | MAELOF | National Grid - NTS | Wales & West Utilities - DN | WN | Ultrasonic
Malpas MRA | Offtake | MALPOF | National Grid - NTS | National Grid - DN | NW | Turbine
Mappowder MTA | Offtake | MAPPOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Market Harborough MTA | Offtake | MKHBOF | National Grid - NTS | National Grid - DN | EM | Orifice
Matching Green MTA | Offtake | MTCHOF | National Grid - NTS | National Grid - DN | EA | Orifice
Melkinthorpe MRA | Offtake | MELKOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Mickle Trafford MTA | Offtake | MICKOF | National Grid - NTS | National Grid - DN | NW | Orifice
Milwich MTA | Offtake | MILWOF | National Grid - NTS | National Grid - DN | WM | Orifice
Nether Howcleugh MRA | Offtake | NETHOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Nether Howcleugh MRB | Offtake | NETHOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pannal MTA | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Ultrasonic
Pannal MTB | Offtake | PANLOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Partington MTA | Offtake | PART OF | National Grid - NTS | National Grid - DN | NW | Orifice
Paull MTA | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Paull MTB | Offtake | PAULOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Peterborough Eye MTA | Offtake | PEYEOF | National Grid - NTS | National Grid - DN | EA | Orifice
Peterborough Eye MTB | Offtake | PEYEOF | National Grid - NTS | National Grid - DN | EA | Orifice
Peterborough Eye MTA/MTB Combined | Offtake | PEYEOF | National Grid - NTS | National Grid - DN | EA | System
Peters Green 2 (South Mimms) MTC | Offtake | PGSMOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green 2 (South Mimms) MTD | Offtake | PGSMOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green 2 (South Mimms) MTC/MTD Combined | Offtake | PGSMOF | National Grid - NTS | National Grid - DN | NT | System
Peters Green 1 MTA | Offtake | PGRNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green 1 MTB | Offtake | PGRNOF | National Grid - NTS | National Grid - DN | NT | Orifice
Peters Green 1 MTA/MTB Combined | Offtake | PGRNOF | National Grid - NTS | National Grid - DN | NT | System
Pickering MTA | Offtake | PICKOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Pitcairngreen MRA | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pitcairngreen MRB | Offtake | PITCOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Pucklechurch MTA | Offtake | PUCKOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Rawcliffe MRA | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Rawcliffe MRB | Offtake | RAWCOF | National Grid - NTS | Northern Gas Networks - DN | NE | Turbine
Ross WM MTA | Offtake | ROSSOF | National Grid - NTS | National Grid - DN | WM | Orifice
Ross-On-Wye MRA | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Ross-On-Wye MRB | Offtake | ROSWOF | National Grid - NTS | Wales & West Utilities - DN | SW | Turbine
Roudham Heath MTA | Offtake | ROUDOF | National Grid - NTS | National Grid - DN | EA | Orifice
Royston MRA | Offtake | ROYSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Royston MRB | Offtake | ROYSOF | National Grid - NTS | National Grid - DN | EA | Turbine
Royston MRA/MRB Combined | Offtake | ROYSOF | National Grid - NTS | National Grid - DN | EA | System
Rugby MTB | Offtake | RUGBOF | National Grid - NTS | National Grid - DN | WM | Orifice
Saltwick 1 | Offtake | SALTOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Samlesbury MTA | Offtake | SAMLOF | National Grid - NTS | National Grid - DN | NW | Orifice
Seabank MTA | Offtake | SEABOF | National Grid - NTS | Wales & West Utilities - DN | SW | Orifice
Shorne MTA | Offtake | SHOROF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Shustoke MTA | Offtake | SHUSOF | National Grid - NTS | National Grid - DN | WM | Orifice
Silk Willoughby MRA | Offtake | SILKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Silk Willoughby MRB | Offtake | SILKOF | National Grid - NTS | National Grid - DN | EM | Turbine
Silk Willoughby MRA/MRB Combined | Offtake | SILKOF | National Grid - NTS | National Grid - DN | EM | System
Soutra MTA | Offtake | SOUTOF | National Grid - NTS | Scotia Gas - DN | SC | Orifice
St Fergus MTA | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
St Fergus MTB | Offtake | FGOTOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRA | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stranraer MRB | Offtake | ZSMFOF & ZSMIOF | National Grid - NTS | Scotia Gas - DN | SC | Turbine
Stratford MRA | Offtake | STRAOF | National Grid - NTS | National Grid - DN | WM | Turbine
Stratford MRB | Offtake | STRAOF | National Grid - NTS | National Grid - DN | WM | Turbine
Sutton Bridge MRA | Offtake | SUTNOF | National Grid - NTS | National Grid - DN | EM | Turbine
Sutton Bridge MRB | Offtake | SUTNOF | National Grid - NTS | National Grid - DN | EM | Turbine
Sutton Bridge MRA/MRB Combined | Offtake | SUTNOF | National Grid - NTS | National Grid - DN | EM | System
Tatsfield MTA | Offtake | TATSOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Thornton Curtis MTA | Offtake | CURTOF | National Grid - NTS | National Grid - DN | EM | Orifice
Thrintoft MTA | Offtake | THRNOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Tow Law MRA | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Tow Law MRB | Offtake | TOWLOF | National Grid - NTS | Northern Gas Networks - DN | NO | Turbine
Towton MTA | Offtake | TOWTOF | National Grid - NTS | Northern Gas Networks - DN | NE | Orifice
Tur Langton MTA | Offtake | TURLOF | National Grid - NTS | National Grid - DN | EM | Orifice
Walesby MRA | Offtake | WSBYOF | National Grid - NTS | National Grid - DN | EM | Turbine
Walesby MRB | Offtake | WSBYOF | National Grid - NTS | National Grid - DN | EM | Turbine
Walesby MRA/MRB Combined | Offtake | WSBYOF | National Grid - NTS | National Grid - DN | EM | System
Warburton MTA | Offtake | WARBOF | National Grid - NTS | National Grid - DN | NW | Orifice
West Winch MTA | Offtake | WINCOF | National Grid - NTS | National Grid - DN | EA | Orifice
Weston Point MTB | Offtake | WESTOF | National Grid - NTS | National Grid - DN | NW | Orifice
Wetheral MTA | Offtake | WETHOF | National Grid - NTS | Northern Gas Networks - DN | NO | Orifice
Whitwell MTA | Offtake | WHITOF | National Grid - NTS | National Grid - DN | EA | Orifice
Whitwell MTB | Offtake | WHITOF | National Grid - NTS | National Grid - DN | EA | Orifice
Whitwell MTA/MTB Combined | Offtake | WHITOF | National Grid - NTS | National Grid - DN | EA | System
Winkfield 2 MTB | Offtake | WNKSOF | National Grid - NTS | Scotia Gas - DN | SO | Orifice
Winkfield MTA | Offtake | WINKOF | National Grid - NTS | Scotia Gas - DN | SE | Orifice
Winkfield NT MTC | Offtake | WINTOF | National Grid - NTS | National Grid - DN | NT | Orifice
Yelverton MTA | Offtake | YELVOF | National Grid - NTS | National Grid - DN | EA | Orifice
| Over/Under Indicator | Error Magnitude |  | Error Status
| Over | High | >= 50 GWh | Error Notified
| Under | Low | < 30 GWh | MER in Compilation
|  | Medium | >= 30, < 50 GWh | SMER in Compilation
MER Published
SMER Published
Awaiting First Available Invoice
Invoiced
Closed / No Rec Required

## Extract for Register
Unique Reference Number | DN Reference | Description | Offtake | LDZ | Downstream Transporter | Significance Low <30GWH Medium >=30<50GWh High >=50GWh | Declared volume of error (MCM) | Estimated quantity of error (GWh) | Discovered | Error First Notified | First Gas Day Where Error Present | Last Gas Day Where Error Present | Latest Notification Update | Latest Error Status | Live/ Closed
WM014 | MER/UKD/182/13 | Incorrect flow computer firmware was used. | Atherstone MRA | WM | National Grid - DN | High | 12.11 | 131.9 | 2013-02-20 | 2013-02-21 | 2012-03-14 | 2013-02-20 | 2013-02-22 | MER in Compilation | Live